## DEP_NoOFW_Needs
Duke Energy Progress - MVST Needs after No Offshore Wind Sensitivity - DRAFT |  |  |  |  | Scenario 1 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 2 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 3 - Summer Cases - Max Branch Loading [%] | [24 empty] | Scenario 1 - Winter Cases - Max Branch Loading [%] | [27 empty] | Scenario 2 - Winter Cases - Max Branch Loading [%] | [25 empty] | Scenario 3 - Winter Cases - Max Branch Loading [%] | [33 empty] | Winter Ratings | Summer Ratings | [9 empty] | Exclusion Criteria | Exclusion Criteria | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point | Score 1 Point per 1000 MW | Exclusion Criteria |  | Exclusion Criteria
[5 empty] | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base - CSM | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Base | Base | Base | Base | Base | Base | Base | Base | Base | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | OFW | OFW | OFW | OFW | OFW | OFW | OFW | Max Base [%] | Max Overload [%] |  |  | Facility Ratings [MVA] |  | Cases with Overloads | [8 empty] | Contains Overloaded Cases |  |  | 2024 CTPC Needs Results | 2024 CTPC Needs Results | 2023 CTPC Needs Results
Branch Identifier | Voltage | Monitored Branch | Line or Substation | Branch Name | ctpc34s_r3_MVST_Scenario1_CSM | ctpc34s_r3_MVST_Scenario1_CSM_br1dn | ctpc34s_r3_MVST_Scenario1_CSM_br2dn | ctpc34s_r3_MVST_Scenario1_CSM_hardn | ctpc34s_r3_MVST_Scenario1_CSM_rob2dn | ctpc34s_r3_MVST_Scenario1_SP | ctpc34s_r3_MVST_Scenario1_SP_br1dn | ctpc34s_r3_MVST_Scenario1_SP_br2dn | ctpc34s_r3_MVST_Scenario1_SP_hardn | ctpc34s_r3_MVST_Scenario1_S90 | ctpc34s_r3_MVST_Scenario1_S90_br1dn | ctpc34s_r3_MVST_Scenario1_S90_br2dn | ctpc34s_r3_MVST_Scenario1_S90_hardn | ctpc34s_r3_MVST_Scenario1_S90_rob2dn | ctpc34s_r3_MVST_Scenario1_S110 | ctpc34s_r3_MVST_Scenario1_S110_br1dn | ctpc34s_r3_MVST_Scenario1_S110_br2dn | ctpc34s_r3_MVST_Scenario1_S110_hardn | ctpc34s_r3_MVST_Scenario1_S110_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW | ctpc34s_r3_MVST_Scenario1_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario1_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario1_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario1_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_CSM | ctpc34s_r3_MVST_Scenario2_CSM_br1dn | ctpc34s_r3_MVST_Scenario2_CSM_br2dn | ctpc34s_r3_MVST_Scenario2_CSM_hardn | ctpc34s_r3_MVST_Scenario2_CSM_rob2dn | ctpc34s_r3_MVST_Scenario2_SP | ctpc34s_r3_MVST_Scenario2_SP_br1dn | ctpc34s_r3_MVST_Scenario2_SP_br2dn | ctpc34s_r3_MVST_Scenario2_SP_hardn | ctpc34s_r3_MVST_Scenario2_SP_rob2dn | ctpc34s_r3_MVST_Scenario2_S90 | ctpc34s_r3_MVST_Scenario2_S90_br1dn | ctpc34s_r3_MVST_Scenario2_S90_br2dn | ctpc34s_r3_MVST_Scenario2_S90_hardn | ctpc34s_r3_MVST_Scenario2_S90_rob2dn | ctpc34s_r3_MVST_Scenario2_S110 | ctpc34s_r3_MVST_Scenario2_S110_br1dn | ctpc34s_r3_MVST_Scenario2_S110_br2dn | ctpc34s_r3_MVST_Scenario2_S110_hardn | ctpc34s_r3_MVST_Scenario2_S110_rob2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW | ctpc34s_r3_MVST_Scenario2_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario2_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario2_SP_OFW_rob2dn | ctpc34s_r3_MVST_Scenario3_CSM | ctpc34s_r3_MVST_Scenario3_CSM_br1dn | ctpc34s_r3_MVST_Scenario3_CSM_br2dn | ctpc34s_r3_MVST_Scenario3_CSM_hardn | ctpc34s_r3_MVST_Scenario3_CSM_rob2dn | ctpc34s_r3_MVST_Scenario3_SP | ctpc34s_r3_MVST_Scenario3_SP_br1dn | ctpc34s_r3_MVST_Scenario3_SP_br2dn | ctpc34s_r3_MVST_Scenario3_SP_hardn | ctpc34s_r3_MVST_Scenario3_SP_rob2dn | ctpc34s_r3_MVST_Scenario3_S90 | ctpc34s_r3_MVST_Scenario3_S90_br1dn | ctpc34s_r3_MVST_Scenario3_S90_br2dn | ctpc34s_r3_MVST_Scenario3_S90_hardn | ctpc34s_r3_MVST_Scenario3_S90_rob2dn | ctpc34s_r3_MVST_Scenario3_S110 | ctpc34s_r3_MVST_Scenario3_S110_br1dn | ctpc34s_r3_MVST_Scenario3_S110_br2dn | ctpc34s_r3_MVST_Scenario3_S110_hardn | ctpc34s_r3_MVST_Scenario3_S110_rob2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW | ctpc34s_r3_MVST_Scenario3_SP_OFW_br1dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_br2dn | ctpc34s_r3_MVST_Scenario3_SP_OFW_hardn | ctpc34s_r3_MVST_Scenario3_SP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP | ctpc34w_r3_MVST_Scenario1_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_br1dn | ctpc34w_r3_MVST_Scenario1_WP_br2dn | ctpc34w_r3_MVST_Scenario1_WP_hardn | ctpc34w_r3_MVST_Scenario1_WP_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_waltdn | ctpc34w_r3_MVST_Scenario1_W90 | ctpc34w_r3_MVST_Scenario1_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W90_br1dn | ctpc34w_r3_MVST_Scenario1_W90_br2dn | ctpc34w_r3_MVST_Scenario1_W90_hardn | ctpc34w_r3_MVST_Scenario1_W90_rob2dn | ctpc34w_r3_MVST_Scenario1_W90_waltdn | ctpc34w_r3_MVST_Scenario1_W110 | ctpc34w_r3_MVST_Scenario1_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario1_W110_br1dn | ctpc34w_r3_MVST_Scenario1_W110_br2dn | ctpc34w_r3_MVST_Scenario1_W110_hardn | ctpc34w_r3_MVST_Scenario1_W110_rob2dn | ctpc34w_r3_MVST_Scenario1_W110_waltdn | ctpc34w_r3_MVST_Scenario1_WP_OFW | ctpc34w_r3_MVST_Scenario1_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario1_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario1_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP | ctpc34w_r3_MVST_Scenario2_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_br1dn | ctpc34w_r3_MVST_Scenario2_WP_br2dn | ctpc34w_r3_MVST_Scenario2_WP_hardn | ctpc34w_r3_MVST_Scenario2_W90 | ctpc34w_r3_MVST_Scenario2_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W90_br1dn | ctpc34w_r3_MVST_Scenario2_W90_br2dn | ctpc34w_r3_MVST_Scenario2_W90_hardn | ctpc34w_r3_MVST_Scenario2_W90_rob2dn | ctpc34w_r3_MVST_Scenario2_W90_waltdn | ctpc34w_r3_MVST_Scenario2_W110 | ctpc34w_r3_MVST_Scenario2_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario2_W110_br1dn | ctpc34w_r3_MVST_Scenario2_W110_br2dn | ctpc34w_r3_MVST_Scenario2_W110_hardn | ctpc34w_r3_MVST_Scenario2_W110_rob2dn | ctpc34w_r3_MVST_Scenario2_W110_waltdn | ctpc34w_r3_MVST_Scenario2_WP_OFW | ctpc34w_r3_MVST_Scenario2_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario2_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_OFW_waltdn | ctpc34w_r3_MVST_Scenario2_WP_rob2dn | ctpc34w_r3_MVST_Scenario2_WP_waltdn | ctpc34w_r3_MVST_Scenario3_WP | ctpc34w_r3_MVST_Scenario3_WP_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_br1dn | ctpc34w_r3_MVST_Scenario3_WP_br2dn | ctpc34w_r3_MVST_Scenario3_WP_hardn | ctpc34w_r3_MVST_Scenario3_WP_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_waltdn | ctpc34w_r3_MVST_Scenario3_W90 | ctpc34w_r3_MVST_Scenario3_W90_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W90_br1dn | ctpc34w_r3_MVST_Scenario3_W90_br2dn | ctpc34w_r3_MVST_Scenario3_W90_hardn | ctpc34w_r3_MVST_Scenario3_W90_rob2dn | ctpc34w_r3_MVST_Scenario3_W90_waltdn | ctpc34w_r3_MVST_Scenario3_W110 | ctpc34w_r3_MVST_Scenario3_W110_ashcc1dn | ctpc34w_r3_MVST_Scenario3_W110_br1dn | ctpc34w_r3_MVST_Scenario3_W110_br2dn | ctpc34w_r3_MVST_Scenario3_W110_hardn | ctpc34w_r3_MVST_Scenario3_W110_rob2dn | ctpc34w_r3_MVST_Scenario3_W110_waltdn | ctpc34w_r3_MVST_Scenario3_WP_OFW | ctpc34w_r3_MVST_Scenario3_WP_OFW_ashcc1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br1dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_br2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_hardn | ctpc34w_r3_MVST_Scenario3_WP_OFW_rob2dn | ctpc34w_r3_MVST_Scenario3_WP_OFW_waltdn | Total | Grand Total | CSM - No OFW | WP - No OFW | Base Rate | Rate Cont | Scenario 1 Summer | Scenario 2 Summer | Scenario 3 Summer | Scenario 1 Winter | Scenario 2 Winter | Scenario 3 Winter | 1 | 2 | 3 | # of Scenarios (3) | # of Base Cases (50, incl TRM cases) | Load Sensitive | Base Case Reliability Loading [%] | Economic Study Loading [%] | Public Policy Study Loading [%] | Generation MW | Major Component Limited | Score | Existing Project | Solution Notes
304248,306542,1 | 230 | 304248 ANSONVILLE 230 306542 6OAKBORO 230 1 | Line | Lilesville - DPC Oakboro 230kV Black | 139.4 | 113.33 | 113.62 | 115.14 | 114.02 | 126.75 | 100.98 | 101.25 | 102.74 | 127.2 | 101 | 101.28 | 102.79 | 101.68 | 156.99 | 130.24 | 130.53 | 132.19 | 130.9 | 175.83 | 149.88 | 150.11 | 151.51 | 150.43 | 101.7 | 151.62 | 126.13 | 126.42 | 128.05 | 126.9 | 99.38 | [9 empty] | 118.14 | 92.38 | 92.66 | 94.13 | 93.19 | 133.88 | 108.85 | 109.06 | 110.53 | 109.34 | 189.71 | 163.9 | 164.2 | 165.71 | 164.57 | 158.17 | 132.23 | 132.51 | 134.09 | 132.8 | 148.64 | 122.62 | 122.9 | 124.45 | 123.13 | 172.42 | 145.71 | 145.98 | 147.65 | 146.16 | 167.96 | 143.12 | 143.32 | 144.54 | 143.44 | [21 empty] | 108.17 | 107.52 |  |  |  |  | 107.34 | [42 empty] | 102 | 101.36 |  |  |  |  | 101.16 | 108.2 | 107.55 |  |  |  |  | 107.39 | 158.17 | 189.71 | 121.68 |  | 398 | 398 | 25 | 11 | 25 | 3 | 0 | 6 | 28 | 11 | 31 | 3 | 24 | YES |  |  | 131.83 | 16647.82 | Yes | 19 | Yes | RZEP 2.0 - Rebuild with 6-1272 ACSR (1083 MVA) - ISD 6/1/2028
304985,305049,1 | 230 | 304985 LILES SS TT 230 305049 E11-BURNSVL 230 1 | Line | Lilesville - DPC Oakboro 230kV White | 129.76 | 105.41 | 105.68 | 107.12 | 106.09 | 117.18 | 93.18 | 93.43 | 94.83 | 117.64 | 93.23 | 93.49 | 94.9 | 93.89 | 145.54 | 120.56 | 120.84 | 122.39 | 121.19 | 163.15 | 139.02 | 139.23 | 140.54 | 139.54 | 93.88 | 143.45 | 119.61 | 119.88 | 121.42 | 120.34 | 94.63 | [9 empty] | 112.26 |  |  |  |  | 126.9 | 103.48 | 103.68 | 105.07 | 103.94 | 175.25 | 151.32 | 151.6 | 153.02 | 151.99 | 146.49 | 122.32 | 122.59 | 124.08 | 122.88 | 137.61 | 113.43 | 113.7 | 115.15 | 113.94 | 159.99 | 134.98 | 135.24 | 136.81 | 135.43 | 155.74 | 132.58 | 132.77 | 133.94 | 132.9 | [21 empty] | 99.38 | 98.78 |  |  |  |  | 98.6 | [42 empty] | 94.73 | 94.13 |  |  |  |  | 93.95 | 100.47 | 99.87 |  |  |  |  | 99.72 | 146.49 | 175.25 | 115.43 |  | 397 | 397 | 17 | 11 | 25 | 0 | 0 | 1 | 17 | 11 | 26 | 3 | 21 | YES |  |  | 125.03 | 15740.21 | Yes | 18 | Yes | RZEP 2.0 - Rebuild with 6-1272 ACSR (1083 MVA) - ISD 6/1/2028
305049,306542,1 | 230 | 305049 E11-BURNSVL 230 306542 6OAKBORO 230 1 | Line | Lilesville - DPC Oakboro 230kV White | 127.03 | 102.73 | 103 | 104.43 | 103.4 | 114.33 | 90.38 | 90.64 | 92.03 | 115.07 | 90.71 | 90.98 | 92.38 | 91.37 | 142.3 | 117.4 | 117.68 | 119.23 | 118.04 | 160.19 | 136.12 | 136.33 | 137.63 | 136.64 | 91.08 | 140.67 | 116.89 | 117.16 | 118.69 | 117.61 | 91.82 | [9 empty] | 109.07 |  |  |  |  | 124.01 | 100.65 | 100.85 | 102.23 | 101.11 | 172.41 | 148.54 | 148.81 | 150.23 | 149.2 | 143.52 | 119.43 | 119.7 | 121.19 | 120 | 135 | 110.88 | 111.14 | 112.59 | 111.38 | 156.6 | 131.72 | 131.98 | 133.54 | 132.17 | 152.77 | 129.68 | 129.87 | 131.04 | 130 | [21 empty] | 96.59 | 95.99 |  |  |  |  | 95.81 | [42 empty] | 91.61 | 91.01 |  |  |  |  | 90.83 | 97.67 | 97.08 |  |  |  |  | 96.92 | 143.52 | 172.41 | 112.73 |  | 398 | 398 | 17 | 11 | 25 | 0 | 0 | 0 | 17 | 11 | 25 | 3 | 21 | YES |  |  | 121.93 | 15740.21 | Yes | 18 | Yes | RZEP 2.0 - Rebuild with 6-1272 ACSR (1083 MVA) - ISD 6/1/2028
304451,314574,1 | 230 | 304451 GREENVILE TT 230 314574 6EVERETS 230 1 | Line | Greenville - VP Everetts 230kV | 108.94 |  |  | 93.01 | [15 empty] | 99.97 | [5 empty] | 102.58 | [24 empty] | 107 |  |  | 90.11 | [16 empty] | 106.83 | [88 empty] | 0 | 108.94 |  |  | 476 | 476 | 1 | 1 | 2 | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 3 | NO | 119.22 |  |  | 9290.65 | No | 11 | Yes | Greenville - VEPCO Everetts 230 kV Line, Reconductor Entire Line - ISD 12/1/2026
304022,304610,1 | 230 | 304022 BRUN1 230 TT 230 304610 SPRT &PA TAP 230 1 | Line | Brunswick Unit 1 - Delco 230kV East | 94.9 |  | 105.58 | 91.24 | 90.04 | 100.26 |  | 111.52 | 97.47 | 98.05 |  | 108.84 | 94.86 | 92.81 | 103.09 |  | 114.89 | 100.59 | 98.64 | 109.39 |  | 117.31 | 119.45 | 117.08 | 95.49 | 95.06 |  | 106.77 | 92.53 | 90.8 | 99.45 |  | 110.34 | 96.39 | 94.32 | 97.05 |  | 107.34 | 93.47 | 91.35 | 102.16 |  | 113.65 | 99.41 | 97.39 | 109.4 |  | 116.73 | 118.99 | 116.48 | 95.52 |  | 106.99 | 92.61 | 90.94 | 99.15 |  | 110.71 | 96.56 | 94.65 | 96.97 |  | 108.06 | 94.09 | 92.13 | 90.66 |  | 102.94 |  |  | 114.2 |  | 119.53 | 106.55 | 120.8 | 96.36 | 96.34 |  | 107.66 | 93.76 | 91.81 | 96.34 | 93.93 | 93.91 |  | 103.54 | 90.98 |  | 93.91 | 99.04 | 99.01 |  | 111.61 | 96.78 | 94.63 | 99.01 | 94.58 | 94.57 |  | 100.73 | 101.39 | 99.42 | 94.56 | 95.68 | 95.66 |  | 106.08 | 92.68 | 93.24 | 93.23 |  | 102.1 |  |  | 93.23 | 98.16 | 98.13 |  | 109.59 | 95.55 | 93.33 | 98.13 | 95.47 | 95.48 |  | 100.74 | 101.7 | 99.71 | 95.47 | 90.65 | 95.66 |  |  |  | 97.03 | [6 empty] | 94.35 | [6 empty] | 97.8 |  |  |  | 96.54 | 96.55 |  | 101.94 | 103.16 | 101.1 | 96.54 | 111.52 | 120.8 | 99.47 | 108.84 | 648 | 648 | 11 | 9 | 8 | 3 | 3 | 3 | 14 | 12 | 11 | 3 | 9 | YES |  |  |  | 7273.49 | Yes | 9 | Yes | B23006 - Reconductor 0.09 mi Brunswick 1 - Southport Tap section of Brunswick 1 - Delco 230 kV East line with 6-1590 MCM ACSR, upgrade switch #1-2 to 3000 A, and upgrade wave trap, CT ratios, and relay settings at the Brunswick end to at least 2200 A - ISD 6/1/2030
304022,304046,1 | 230 | 304022 BRUN1 230 TT 230 304046 WSPOON230 TT 230 1 | Line | Brunswick Unit 1 - Weatherspoon Plant 230kV | 90.6 | [18 empty] | 127.63 |  |  | 118.89 | 118.64 | [21 empty] | 130.68 |  | 91.98 | 121.07 | 120.57 | [20 empty] | 142.78 |  | 99.66 | 127.1 | 130.07 | [21 empty] | 93.99 | 94.14 |  |  |  |  | 94.12 | [19 empty] | 100.9 | 101.05 |  |  | 93.27 | 93.61 | 101.02 | [23 empty] | 104.25 | 104.34 |  |  | 95.96 | 96.27 | 104.3 | 0 | 142.78 | 0 | 92.15 | 478 | 478 | 3 | 3 | 3 | 0 | 3 | 3 | 3 | 6 | 6 | 3 | 0 | NO |  |  |  | 7520.46 | Yes | 8 | No | Monitor - Substation upgrades (relay, wave trap, switches) to get full winter conductor rating (683 MVA)
304610,305010,1 | 230 | 304610 SPRT &PA TAP 230 305010 E1-BOLIVIA 230 1 | Line | Brunswick Unit 1 - Delco 230kV East |  |  | 94.78 |  |  |  |  | 100.3 |  |  |  | 98.38 |  |  | 91.19 |  | 102.92 |  |  | 97.61 |  | 105.76 | 107.2 | 104.95 |  |  |  | 95.95 |  |  |  |  | 99.12 |  |  |  |  | 96.88 |  |  | 90.25 |  | 101.68 |  |  | 97.58 |  | 105.15 | 106.7 | 104.34 |  |  | 96.13 |  |  |  |  | 99.53 |  |  |  |  | 97.59 |  |  |  |  | 91.07 |  |  | 101.96 |  | 107.79 | 94.82 | 108.29 |  |  |  | 98.9 | [6 empty] | 95.59 | [6 empty] | 102.07 |  |  |  | 0 | 0 |  | 91.88 | 92.14 | 90.23 | 0 |  |  |  | 97.33 |  |  |  |  | 94.18 | [6 empty] | 100.11 |  |  |  | 0 | 0 |  | 91.87 | 92.39 | 90.46 | 0 | [23 empty] | 0 | 0 |  | 93.02 | 93.77 | 91.77 | 0 | 100.3 | 108.29 | 88.66 | 99.28 | 637 | 637 | 5 | 4 | 3 | 1 | 1 | 0 | 6 | 5 | 3 | 3 | 1 | YES |  |  |  | 5614.38 | Yes | 7 | Yes | B23016 - Upgrade switch on Brunswick 1-Delco 230 East line (736 MVA) - ISD 6/1/2030
304500,304510,2 | 230 | 304500 WOMMACK230TT 230 304510 WOMACKW115TT 115 2 | Substation | Wommack 230kV | [15 empty] | 92.69 | 91.83 | [14 empty] | 92.33 | 91.42 | [7 empty] | 95.35 | 100.14 | 99.45 | 93.21 | 93.75 | [30 empty] | 114.51 | 114.54 | 119.21 | 118.19 | 111.54 | 112.01 | 114.54 | 104.99 | 105.02 | 109.28 | 108.26 | 101.76 | 102.19 | 105.01 | 122.59 | 122.61 | 127.67 | 126.65 | 119.87 | 120.37 | 122.61 | 98.01 | 98.04 | 101.15 | 101.1 | 95.54 | 96.14 | 98.04 | 100.11 | 100.14 | 105.33 | 104.31 | 97.76 | 90.79 | 90.82 | 95.8 | 94.77 |  |  | 90.82 | 108.39 | 108.41 | 113.98 | 112.94 | 106.25 | 106.87 | 108.41 | [7 empty] | 98.2 | 100.13 | 109.48 | 109.5 | 114.07 | 113.06 | 106.73 | 107.31 | 109.5 | 99.91 | 99.93 | 104.16 | 103.16 | 96.96 | 97.49 | 99.93 | 117.91 | 117.94 | 122.57 | 121.58 | 115.33 | 115.9 | 117.93 | 96.62 | 96.65 | 99.98 | 99.91 | 94.28 | 94.97 | 96.64 | 119.21 | 127.67 |  | 83.93 | 200 | 200 | 0 | 1 | 0 | 9 | 8 | 7 | 9 | 9 | 7 | 3 | 19 | YES |  |  |  | 2725.04 | Yes | 4 | No | Monitor - Transformer would need to be replaced.
304500,304507,1 | 230 | 304500 WOMMACK230TT 230 304507 WOMACKE115TT 115 1 | Substation | Wommack 230kV | [15 empty] | 91.74 | 91.28 | [8 empty] | 91.5 | 94.47 | 94 |  |  | 93.58 | 97.51 | 97 | 92.05 | 91.87 | [5 empty] | 95.88 | 100.04 | 99.52 | 94.67 | 94.53 | [30 empty] | 99.58 | 99.61 | 103.53 | 102.93 | 98.15 | 97.85 | 99.6 | 90.64 | 90.67 | 94.42 | 93.84 |  |  | 90.66 | 98.21 | 98.25 | 102.83 | 102.26 | 97.3 | 97.16 | 98.23 | [9 empty] | 93.03 | 92.44 | [10 empty] | 92.55 | 91.95 | [14 empty] | 94.3 | 93.72 | [10 empty] | 93.1 | 93.13 | 97.86 | 97.3 | 92.49 | 92.47 | 93.11 | [7 empty] | 103.53 | 103.53 |  |  | 224 | 224 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 1 | 0 | 2 | 2 | NO |  |  |  | 3308.54 | Yes | 4 | No | Monitor - Potential to address with emergency ratings
304342,339001,1 | 115 | 304342 BADIN #1 115 339001 BADIN 100 1 | Substation | Badin Transformer 115kV/100kV #1 | 126.75 | 100.17 | 100.28 | 95.15 | 101.44 | 126.06 | 99.62 | 99.72 | 94.83 | 133.47 | 106.68 | 106.79 | 101.96 | 107.85 | 146.04 | 119.55 | 119.67 | 114.6 | 120.88 | 173.98 | 147.66 | 147.78 | 142.58 | 149.02 | 100.87 | 138.64 | 113.61 | 113.72 | 108.2 | 114.85 | [10 empty] | 96.5 |  |  |  |  | 116.81 | 92.34 | 92.5 |  | 93.58 | 180.86 | 155.57 | 155.69 | 150.69 | 156.79 | 137.45 | 112.42 | 112.53 | 107.5 | 113.67 | 130.45 | 104.91 | 105.02 | 100.11 | 106.08 | 150.48 | 125.64 | 125.75 | 120.35 | 126.95 | 156.31 | 132.5 | 132.61 | 126.79 | 133.71 | 109.54 | 108.47 |  |  |  |  | 108.27 | 111.11 | 110.11 |  |  |  |  | 110 | 117.19 | 116.04 | 90.97 | 91.01 |  | 92.39 | 115.85 | 149.58 | 148.42 | 123.9 | 123.99 | 118.96 | 125.27 | 148.25 | [28 empty] | 96.39 | 95.21 |  |  |  |  | 95.06 | 98.85 | 97.7 |  |  |  |  | 97.59 | 113.03 | 111.85 |  |  |  |  | 111.78 | 122.66 | 121.48 | 97.79 | 97.89 | 93.07 | 99.26 | 121.32 | 137.45 | 180.86 | 103.05 |  | 100 | 100 | 21 | 6 | 25 | 10 | 0 | 6 | 31 | 6 | 31 | 3 | 23 | YES |  |  | 132.99 | 653.9 | Yes | 3 | No | Badin Cluster
304343,339001,1 | 115 | 304343 BADIN #2 115 339001 BADIN 100 1 | Substation | Badin Transformer 115kV/100kV #2 | 120.39 | 95.67 | 95.77 | 90.84 | 96.92 | 119.63 | 94.38 | 94.47 |  | 126.62 | 100.81 | 100.91 | 96.31 | 101.93 | 139.4 | 113.62 | 113.74 | 108.93 | 114.87 | 166.19 | 140.56 | 140.68 | 135.73 | 141.85 | 95.58 | 132.53 | 107.66 | 107.77 | 102.74 | 108.88 | [10 empty] | 93.5 |  |  |  |  | 112.33 |  |  |  |  | 172.31 | 147.54 | 147.65 | 142.78 | 148.73 | 132.25 | 107.63 | 107.73 | 102.97 | 108.81 | 123.89 | 99.06 | 99.17 | 94.42 | 100.2 | 144.47 | 119.72 | 119.83 | 114.82 | 120.95 | 149.82 | 125.36 | 125.48 | 120.24 | 126.54 | 105.99 | 104.97 |  |  |  |  | 104.78 | 106.7 | 105.68 |  |  |  |  | 105.57 | 113.06 | 111.99 |  |  |  |  | 111.82 | 143.8 | 142.74 | 119.54 | 119.61 | 114.82 | 120.84 | 142.58 | [28 empty] | 92.58 | 91.48 |  |  |  |  | 91.33 | 94.54 | 93.44 |  |  |  |  | 93.34 | 106.65 | 105.59 |  |  |  |  | 103.36 | 116.72 | 115.67 | 93.78 | 93.88 |  | 95.2 | 115.52 | 132.25 | 172.31 | 98.65 |  | 100 | 100 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | YES |  |  | 120.61 | 640.3 | Yes | 3 | No | Badin Cluster
304734,306416,1 | 115 | 304734 WATEREE115TT 115 306416 WATEREE 100 1 | Substation | Wateree Plant | [5 empty] | 91.13 | [8 empty] | 107.33 | 98.89 | 98.72 | 103.49 |  | 117.32 | 109.07 | 108.87 | 113.58 | 93.72 |  | 109.51 | 102.47 | 102.3 | 106.65 |  | 113.89 | 107.06 | 106.89 | 111.3 | 92.89 | 102.55 | 95.31 | 95.13 | 99.49 |  | 93.74 |  |  | 91.41 |  | 126.74 | 120.42 | 120.22 | 124.56 | 106.11 | 123.97 | 118.52 | 118.37 | 122.41 | 105.29 | 129.83 | 124.59 | 124.43 | 128.46 | 111.26 | 123.98 | 117.98 | 117.81 | 121.9 | 104.19 | 111.28 | 106.57 | 106.42 | 110.44 | 93.42 | 140.42 | 135.52 | 135.34 | 139.3 | 121.84 | [56 empty] | 95.15 | 94.24 |  |  | 93.85 |  | 94.12 | 91.61 | 90.62 |  |  |  |  | 90.54 | [7 empty] | 106.18 | 105.3 | 101.03 | 100.85 | 105.12 |  | 105.18 | 129.83 | 140.42 | 103.06 |  | 168 | 168 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | NO |  |  | 146.61 | 1294.29 | Yes | 3 | No | Wateree Cluster
304734,306416,2 | 115 | 304734 WATEREE115TT 115 306416 WATEREE 100 2 | Substation | Wateree Plant | [5 empty] | 91.13 | [8 empty] | 107.33 | 98.89 | 98.72 | 103.49 |  | 117.32 | 109.07 | 108.87 | 113.58 | 93.72 |  | 109.51 | 102.47 | 102.3 | 106.65 |  | 113.89 | 107.06 | 106.89 | 111.3 | 92.89 | 102.55 | 95.31 | 95.13 | 99.49 |  | 93.74 |  |  | 91.41 |  | 126.74 | 120.42 | 120.22 | 124.56 | 106.11 | 123.97 | 118.52 | 118.37 | 122.41 | 105.29 | 129.83 | 124.59 | 124.43 | 128.46 | 111.26 | 123.98 | 117.98 | 117.81 | 121.9 | 104.19 | 111.28 | 106.57 | 106.42 | 110.44 | 93.42 | 140.42 | 135.52 | 135.34 | 139.3 | 121.84 | [56 empty] | 95.15 | 94.24 |  |  | 93.85 |  | 94.12 | 91.61 | 90.62 |  |  |  |  | 90.54 | [7 empty] | 106.18 | 105.3 | 101.03 | 100.85 | 105.12 |  | 105.18 | 129.83 | 140.42 | 103.06 |  | 168 | 168 | 6 | 14 | 24 | 0 | 0 | 6 | 6 | 14 | 30 | 3 | 18 | NO |  |  | 146.61 | 1294.29 | Yes | 3 | No | Wateree Cluster
304088,304089,2 | 230 | 304088 HENDER 230TT 230 304089 HENDER 115TT 115 2 | Substation | Henderson 230kV | [103 empty] | 105.2 | 105.3 | 103.38 | 103.23 | 103.6 | [7 empty] | 109.25 | 109.34 | 107.89 | 107.75 | 108.32 | 105.92 | 109.35 | 99.71 | 99.8 | 98.51 | 98.38 | 98.71 | 96.58 | 99.81 | 101.36 | 105.31 | 104.87 | 104.96 | 103.43 | 103.28 | 103.56 | 101.5 | 104.97 | [7 empty] | 108.68 | 108.77 | 107.46 | 107.33 | 107.83 | 105.58 | 108.78 | 101.41 | 101.5 | 100.34 | 100.21 | 100.5 | 98.42 | 101.51 | 105.31 | 109.35 |  | 108.3 | 239 | 239 | 0 | 0 | 0 | 0 | 9 | 13 | 0 | 9 | 13 | 2 | 14 | YES |  |  |  | 1702 | No | 3 | Yes | Henderson 230/115 kV Banks #1 & #2, Upgrade CT Ratios and Relay Settings (336 MVA) - ISD 12/1/2025
304731,304732,1 | 115 | 304731 CAMD DUP TT 115 304732 ELGIN TAP 115 1 | Line | Camden DuPont - DPC Wateree Plant 115kV | 124.42 | 113.24 | 112.96 | 119.92 | 92.42 | 149.11 | 137.53 | 137.22 | 144.57 | 145.07 | 132.87 | 132.55 | 139.96 | 110.4 | 176.41 | 164.33 | 164.03 | 171.57 | 141.65 | 190.39 | 178.46 | 178.13 | 185.6 | 155.43 | 115.08 | 175.71 | 165.02 | 164.73 | 171.8 | 143.99 | 192.27 | 182.38 | 182.05 | 189 | 164.24 | 171.26 | 160.77 | 160.46 | 167.41 | 141.7 | 157.95 | 150.19 | 149.93 | 156.26 | 132.86 | 212.66 | 202.8 | 202.45 | 209.72 | 181.38 | 198.64 | 190.03 | 189.73 | 196.39 | 169.44 | 218.98 | 209.97 | 209.69 | 216.51 | 189.06 | 204.56 | 195.21 | 194.92 | 201.59 | 174.14 | 186.77 | 179.05 | 178.79 | 185.4 | 159.5 | 235.87 | 226.54 | 226.21 | 233.35 | 204.92 | 91.21 | [20 empty] | 112.03 | 110.6 | 104.29 | 104.03 | 109.81 |  | 110.4 | [19 empty] | 107.57 | 106.19 | 102.07 | 101.81 | 107.14 |  | 106.02 |  |  | 125.94 | 124.65 | 119.57 | 119.33 | 124.92 | 103.79 | 124.49 | 119.82 | 118.49 | 111.56 | 111.33 | 116.88 | 95.11 | 118.39 | 99.74 | 98.48 | 93.02 | 92.84 | 98.4 |  | 98.27 | 139.63 | 138.37 | 133.57 | 133.33 | 138.81 | 115.75 | 138.22 | 218.98 | 235.87 | 162.35 |  | 94 | 94 | 24 | 25 | 25 | 6 | 6 | 20 | 30 | 31 | 45 | 3 | 35 | NO |  |  | 230.11 | 810.89 | Yes | 2 | No | Wateree Cluster
304248,304358,1 | 230 | 304248 ANSONVILLE 230 304358 WADESBOW TAP 230 1 | Line | Lilesville - DPC Oakboro 230kV Black | 134.78 | 109.23 | 109.53 | 111.03 | 110.03 | 119.86 | 94.48 | 94.76 | 96.22 | 120.45 | 94.66 | 94.95 | 96.44 | 95.45 | 149.93 | 123.62 | 123.92 | 125.56 | 124.37 | 169.07 | 143.54 | 143.76 | 145.15 | 144.16 | 95.3 | 153.66 | 128.1 | 128.39 | 130.03 | 128.87 | 101.31 | [9 empty] | 120.15 | 94.31 | 94.59 | 96.06 | 95.12 | 135.9 | 110.79 | 111.01 | 112.48 | 111.28 | 179.9 | 154.87 | 155.17 | 156.67 | 155.68 | 150.96 | 125.53 | 125.82 | 127.38 | 126.21 | 141.85 | 116.36 | 116.65 | 118.17 | 116.98 | 164.96 | 138.81 | 139.09 | 140.76 | 139.36 | 160.98 | 136.52 | 136.72 | 137.99 | 136.92 | [21 empty] | 100.52 | 99.89 |  |  |  |  | 99.7 | [42 empty] | 98.24 | 97.61 |  |  |  |  | 97.41 | 104.48 | 103.84 |  |  |  |  | 103.68 | 150.96 | 179.9 | 123.65 |  | 397 | 397 | 17 | 12 | 25 | 1 | 0 | 3 | 18 | 12 | 28 | 3 | 22 | YES |  |  | 133.79 |  | Yes | 2 | Yes | RZEP 2.0 - Rebuild with 6-1272 ACSR (1083 MVA) - ISD 6/1/2028
304358,304985,1 | 230 | 304358 WADESBOW TAP 230 304985 LILES SS TT 230 1 | Line | Lilesville - DPC Oakboro 230kV Black | 134.81 | 109.28 | 109.57 | 111.07 | 110.07 | 119.87 | 94.5 | 94.78 | 96.24 | 120.47 | 94.69 | 94.98 | 96.47 | 95.48 | 149.93 | 123.62 | 123.92 | 125.56 | 124.37 | 169.07 | 143.54 | 143.77 | 145.15 | 144.17 | 95.32 | 153.67 | 128.11 | 128.4 | 130.05 | 128.89 | 101.31 | [9 empty] | 120.14 | 94.3 | 94.58 | 96.06 | 95.11 | 135.9 | 110.79 | 111.01 | 112.48 | 111.28 | 179.9 | 154.89 | 155.18 | 156.68 | 155.69 | 150.96 | 125.53 | 125.82 | 127.38 | 126.21 | 141.86 | 116.39 | 116.68 | 118.2 | 117.01 | 164.95 | 138.81 | 139.09 | 140.76 | 139.36 | 160.98 | 136.52 | 136.72 | 137.99 | 136.92 | [21 empty] | 100.53 | 99.89 |  |  |  |  | 99.71 | [42 empty] | 98.24 | 97.61 |  |  |  |  | 97.41 | 104.48 | 103.84 |  |  |  |  | 103.68 | 150.96 | 179.9 | 123.65 |  | 397 | 397 | 17 | 12 | 25 | 1 | 0 | 3 | 18 | 12 | 28 | 3 | 22 | YES |  |  | 133.85 |  | Yes | 2 | Yes | RZEP 2.0 - Rebuild with 6-1272 ACSR (1083 MVA) - ISD 6/1/2028
304732,304734,1 | 115 | 304732 ELGIN TAP 115 304734 WATEREE115TT 115 1 | Line | Camden DuPont - DPC Wateree Plant 115kV | 93.08 |  |  |  |  | 111.4 | 102.29 | 102.04 | 107.81 | 108.91 | 99.32 | 99.07 | 104.89 |  | 132.14 | 122.64 | 122.41 | 128.33 | 104.82 | 143.85 | 134.46 | 134.2 | 140.08 | 116.35 |  | 132.97 | 124.61 | 124.39 | 129.91 | 108.19 | 145.14 | 137.38 | 137.12 | 142.59 | 123.12 | 129.42 | 121.18 | 120.94 | 126.4 | 106.17 | 117.95 | 111.85 | 111.66 | 116.6 | 98.36 | 161.17 | 153.45 | 153.17 | 158.89 | 136.6 | 150.87 | 144.2 | 143.94 | 149.15 | 128.08 | 165.95 | 158.93 | 158.71 | 164.09 | 142.49 | 155.54 | 148.23 | 148 | 153.24 | 131.67 | 140.07 | 134.15 | 133.95 | 139.12 | 118.86 | 179.28 | 171.74 | 171.49 | 177.36 | 154.78 | [21 empty] | 93.36 | 92.11 |  |  | 91.41 |  | 91.93 | [28 empty] | 105.43 | 104.31 | 99.87 | 99.67 | 104.56 |  | 104.16 | 100.73 | 99.58 | 93.42 | 93.22 | 98.09 |  | 99.49 | [7 empty] | 117.43 | 116.34 | 112.15 | 111.94 | 116.74 | 96.52 | 116.2 | 165.95 | 179.28 | 122.52 |  | 119 | 119 | 16 | 24 | 25 | 0 | 0 | 6 | 16 | 24 | 31 | 3 | 28 | NO |  |  | 175.45 | 781.04 | Yes | 2 | No | Wateree Cluster
304004,304342,1 | 115 | 304004 TILLERY115TT 115 304342 BADIN #1 115 1 | Line | Tillery Plant - Alcoa Badin 115kV Black | 124.19 | 97.94 | 98.06 | 93.03 | 99.18 | 123.47 | 97.56 | 97.66 | 92.87 | 130.64 | 104.36 | 104.47 | 99.74 | 105.51 | 143.33 | 117.14 | 117.26 | 112.28 | 118.45 | 170.78 | 144.67 | 144.79 | 139.67 | 146.01 | 98.79 | 135.97 | 111.11 | 111.22 | 105.84 | 112.34 | [10 empty] | 95.08 |  |  |  |  | 114.89 | 90.57 | 90.73 |  | 91.79 | 176.87 | 151.47 | 151.59 | 146.7 | 152.7 | 135.62 | 110.46 | 110.57 | 105.62 | 111.68 | 127.74 | 102.53 | 102.64 | 97.83 | 103.68 | 148.22 | 123.12 | 123.23 | 117.95 | 124.4 | 153.63 | 129.37 | 129.48 | 123.85 | 130.56 | 108.03 | 106.96 |  |  |  |  | 106.76 | 109.16 | 108.15 |  |  |  |  | 108.04 | 115.76 | 114.61 |  |  |  | 91.13 | 114.43 | 148.16 | 146.97 | 122.23 | 122.31 | 117.31 | 123.58 | 146.79 | [28 empty] | 95.49 | 94.29 |  |  |  |  | 94.14 | 97.33 | 96.15 |  |  |  |  | 96.04 | 111.52 | 110.33 |  |  |  |  | 110.14 | 121.78 | 120.62 | 96.83 | 96.94 | 92.2 | 98.29 | 120.46 | 135.62 | 176.87 | 101.02 |  | 99 | 99 | 16 | 6 | 24 | 10 | 0 | 6 | 26 | 6 | 30 | 3 | 20 | YES |  |  |  | 653.9 | Yes | 2 | No | Badin Cluster
304004,304343,1 | 115 | 304004 TILLERY115TT 115 304343 BADIN #2 115 1 | Line | Tillery Plant - Alcoa Badin 115kV White | 120.66 | 95.52 | 95.63 | 90.7 | 96.79 | 119.97 | 94.51 | 94.61 |  | 126.91 | 100.85 | 100.96 | 96.34 | 101.99 | 140.37 | 114.06 | 114.18 | 109.34 | 115.32 | 167.59 | 141.31 | 141.43 | 136.43 | 142.61 | 95.73 | 133.26 | 107.61 | 107.73 | 102.85 | 108.86 | [10 empty] | 94.43 |  |  |  |  | 113.25 |  |  |  |  | 172.59 | 146.65 | 146.77 | 141.9 | 147.88 | 133.66 | 108.06 | 108.17 | 103.38 | 109.25 | 124.06 | 98.89 | 99 | 94.21 | 100.02 | 145.9 | 120.01 | 120.13 | 115.18 | 121.17 | 150.97 | 125.12 | 125.24 | 120.23 | 126.32 | 107.12 | 106.03 |  |  |  |  | 105.84 | 107.22 | 106.19 |  |  |  |  | 106.07 | 114.58 | 113.48 |  |  |  | 90.76 | 113.3 | 146.02 | 144.88 | 120.88 | 120.95 | 116.08 | 122.21 | 144.71 | [28 empty] | 93.97 | 92.81 |  |  |  |  | 92.67 | 95.31 | 94.15 |  |  |  |  | 94.05 | 107.7 | 106.62 |  |  |  |  | 105.18 | 118.64 | 117.55 | 95.08 | 95.18 |  | 96.53 | 117.39 | 133.66 | 172.59 | 98.88 |  | 99 | 99 | 16 | 6 | 22 | 10 | 0 | 6 | 26 | 6 | 28 | 3 | 20 | YES |  |  |  | 677.8 | Yes | 2 | No | Badin Cluster
304662,304707,2 | 230 | 304662 FLO SUB230TT 230 304707 FLOSUB115ETT 115 2 | Substation | Florence 230kV | 90.68 | 97.98 | 98.7 | 93.82 |  | 101.43 | 108.59 | 109.31 | 104.58 | 96.45 | 103.67 | 104.38 | 99.63 |  | 106.96 | 114.18 | 114.87 | 110.1 | 97 |  | 96.59 | 97.17 | 92.78 |  | 91.48 |  | 95.83 | 96.53 | 91.95 |  | 103.77 | 111.02 | 111.37 | 107.08 | 94.35 | 97.89 | 104.69 | 105.39 | 100.77 |  | 108.48 | 115.46 | 116.18 | 111.44 | 98.99 | 90.96 | 98 | 98.55 | 94.58 |  |  | 93.11 | 93.83 |  |  | 99.55 | 106.12 | 106.84 | 102.23 |  | 94.17 | 100.74 | 101.43 | 96.84 |  | 102.21 | 108.74 | 109.53 | 104.92 | 92.25 |  | 93.85 | 94.41 | 90.27 |  | 116.57 | 116.43 | 123.52 | 124.21 | 119.26 | 105.62 | 116.44 | 110.39 | 110.25 | 117.26 | 117.92 | 113.1 | 99.52 | 110.26 | 121.44 | 121.3 | 128.54 | 129.23 | 124.2 | 110.48 | 121.32 | 103.24 | 103.09 | 109.81 | 110.37 | 105.88 | 92.68 | 103.1 | 121.25 | 121.12 | 127.87 | 128.54 | 123.69 | 114.64 | 114.52 | 121.34 | 121.82 | 117.22 | 104.01 | 114.53 | 124.66 | 124.52 | 131.41 | 132.06 | 127.21 | 113.65 | 124.54 | 108.26 | 108.13 | 114.68 | 115.23 | 110.64 | 97.62 | 108.15 | 110.51 | 121.14 | 114.23 | 114.09 | 120.99 | 121.44 | 116.92 | 103.6 | 114.11 | 108.78 | 108.64 | 115.42 | 116.09 | 111.45 | 98.23 | 108.66 | 119.77 | 119.64 | 126.38 | 127.06 | 122.3 | 108.72 | 119.66 | 105.48 | 105.36 | 111.77 | 112.31 | 107.64 | 94.76 | 105.37 | 128.54 | 132.06 | 107.59 | 132.13 | 239 | 239 | 10 | 11 | 9 | 13 | 15 | 13 | 23 | 26 | 22 | 3 | 32 | YES |  |  |  | 552.89 | No | 2 | Yes | DISIS - Upgrade Relay Settings to 2000A minimum (796 MVA) - ISD 9/27/2028
304046,304047,1 | 230 | 304046 WSPOON230 TT 230 304047 WSPOON115 TT 115 1 | Substation | Weatherspoon Plant | [75 empty] | 108.96 | 108.92 |  | 100.36 | 106.93 | 102.21 | 108.93 | 106.77 | 106.74 |  | 97.19 | 104.14 | 99.44 | 106.75 | 113.81 | 113.76 |  | 105.84 | 111.97 | 107.41 | 113.77 | 128.4 | 128.36 | 100.46 | 116.81 | 125.85 | 121.01 | 128.38 | 113.58 | 113.54 |  | 104.15 | 110.91 | 110.81 | 110.8 |  | 100.67 | 107.7 | 102.63 | 110.81 | 117.92 | 117.87 |  | 109.22 | 116.02 | 110.72 | 117.88 | 131.99 | 131.95 | 104.25 | 120.36 | 129.49 | 124.46 | 131.96 | 106.1 | 113.55 | 112.24 | 112.2 |  | 103.38 | 110.32 | 105.82 | 112.21 | 110.61 | 110.58 |  | 101.15 | 108.12 | 103.42 | 110.58 | 119.18 | 119.14 |  | 110.47 | 117.54 | 112.6 | 119.16 | 127.25 | 127.21 | 100.65 | 116.8 | 125.33 | 120.64 | 127.23 | 113.58 | 131.99 |  | 110.6 | 224 | 224 | 0 | 0 | 0 | 13 | 15 | 13 | 13 | 15 | 13 | 3 | 18 | YES |  |  |  | 540.1 | Yes | 2 | No | Monitor - Transformer would need to be replaced.
304662,304659,1 | 230 | 304662 FLO SUB230TT 230 304659 FLOSUB115WTT 115 1 | Substation | Florence 230kV |  | 91.58 | 92.58 |  |  | 98.69 | 102.28 | 103.29 | 100.31 | 93.48 | 97.19 | 98.17 | 95.19 |  | 104.25 | 107.78 | 108.78 | 105.78 | 99.03 | 92.48 | 95.83 | 96.6 | 93.91 |  | 93.57 | 91.57 | 94.6 | 95.58 | 92.75 |  | 104.19 | 108.01 | 108.44 | 106.05 | 99.84 | 98.95 | 102.19 | 103.18 | 100.27 | 94.33 | 109.24 | 112.49 | 113.51 | 110.51 | 104.44 | 97.16 | 101.2 | 101.92 | 99.42 | 95.15 | 91.51 | 93.7 | 94.71 | 92.16 |  | 102.84 | 105.82 | 106.83 | 103.91 | 98.02 | 97.45 | 100.46 | 101.45 | 98.53 | 92.9 | 106.6 | 109.54 | 110.59 | 107.69 | 101.86 | 96.3 | 99.24 | 99.97 | 97.04 | 93.04 | 112.8 | 112.74 | 115.96 | 117.01 | 113.89 | 106.85 | 112.75 | 107.02 | 106.96 | 110.18 | 111.18 | 108.16 | 101.12 | 106.97 | 117.85 | 117.78 | 121.04 | 122.11 | 118.9 | 111.81 | 117.79 | 105.91 | 105.84 | 108.89 | 109.7 | 106.91 | 100.05 | 105.85 | 120.31 | 120.25 | 123.01 | 124.03 | 120.97 | 114.45 | 114.39 | 117.39 | 118.13 | 115.41 | 108.5 | 114.4 | 124.87 | 124.81 | 127.62 | 128.61 | 125.59 | 118.46 | 124.82 | 113.72 | 113.66 | 116.6 | 117.38 | 114.36 | 107.5 | 113.67 | 114.27 | 120.26 | 116.75 | 116.69 | 119.76 | 120.45 | 117.79 | 110.78 | 116.7 | 111.31 | 111.25 | 114.25 | 115.24 | 112.34 | 105.42 | 111.26 | 122.19 | 122.13 | 124.88 | 125.89 | 122.92 | 115.76 | 122.14 | 112.05 | 112 | 114.99 | 115.75 | 112.59 | 106.1 | 112 | 124.03 | 128.61 | 97.94 | 125.13 | 239 | 239 | 7 | 14 | 11 | 14 | 16 | 14 | 21 | 30 | 25 | 3 | 32 | YES |  |  |  | 304.99 | No | 2 | Yes | DISIS - Upgrade CT Ratios and Relay Settings to 2000A minimum (796 MVA) - ISD 9/27/2028
304659,304707,Z1 | 115 | 304659 FLOSUB115WTT 115 304707 FLOSUB115ETT 115 Z1 | Substation | Florence 230kV | 93.73 | 98.22 | 99.43 | 94.32 |  | 94.26 | 98.79 | 100.01 | 95.01 | 91.92 | 96.5 | 97.69 | 92.75 |  | 96.78 | 101.41 | 102.58 | 97.54 | [7 empty] | 95.32 | 98.62 | 99.81 | 95.11 |  | 97.45 | 102.14 | 102.83 | 98.49 |  | 95.2 | 99.26 | 100.45 | 95.62 |  | 100.31 | 104.57 | 105.81 | 100.82 |  |  | 90.63 | 91.53 |  |  | 94.67 | 97.23 | 98.43 | 94.13 |  | 95.72 | 99.52 | 100.74 | 95.87 |  | 93.62 | 97.38 | 98.56 | 93.73 |  | 95.99 | 99.7 | 100.98 | 96.18 | [6 empty] | 107.93 | 107.87 | 112.58 | 113.85 | 108.45 | 94.49 | 107.89 | 104.54 | 104.49 | 109.05 | 110.29 | 105.09 | 91.44 | 104.5 | 111.01 | 110.94 | 115.82 | 117.12 | 111.52 | 97.45 | 110.97 | 96.17 | 96.12 | 100.18 | 101.16 | 96.53 |  | 96.14 | 115.15 | 115.09 | 119.53 | 120.78 | 115.44 | 110.74 | 110.69 | 115.37 | 116.23 | 111.41 | 98.15 | 110.71 | 116.79 | 116.72 | 121.27 | 122.45 | 117.18 | 103.09 | 116.75 | 103.06 | 103.01 | 106.8 | 107.75 | 102.91 | 90.2 | 103.03 | 102.11 | 115.11 | 110.19 | 110.13 | 114.5 | 115.32 | 110.65 | 97.88 | 110.15 | 107.39 | 107.34 | 111.56 | 112.78 | 107.89 | 95.3 | 107.36 | 113.88 | 113.82 | 117.83 | 119.09 | 113.93 | 100.68 | 113.84 | 102.71 | 102.67 | 106.22 | 107.14 | 102.28 |  | 102.69 | 120.78 | 122.45 | 106.76 | 122.97 | 239 | 239 | 3 | 7 | 2 | 8 | 15 | 13 | 11 | 22 | 15 | 3 | 23 | YES |  |  |  | 920.49 | No | 2 | Yes | DISIS - Upgrade 1200A Florence 115kV bus tie breaker to 3000A (1195 MVA) - ISD 4/30/2027
304105,305173,1 | 115 | 304105 FRANKLIN TT 115 305173 E18-POCOMOKE 115 1 | Line | Falls - Franklinton 115kV West | 102.49 | 104.46 | 104.52 | 109.37 | 103.58 |  |  |  | 93.33 | [6 empty] | 92.19 | 92.24 | 96.89 | 91.21 |  |  |  | 91.64 |  |  | 109.42 | 111.29 | 111.35 | 116.33 | 110.2 | 93.11 | 95.21 | 95.25 | 100.59 | 94.01 | [5 empty] | 95.48 | 97.78 | 97.83 | 103.05 | 96.64 | 90.17 | 91.66 | 91.56 | 97.66 | 90.77 | 106.9 | 109.34 | 109.39 | 114.1 | 108.23 |  | 90.63 | 90.68 | 95.33 | [6 empty] | 90.62 | 93.21 | 93.26 | 98.33 | 92.22 |  |  |  | 94.26 | [85 empty] | 100.59 | 116.33 | 111.78 |  | 170 | 170 | 5 | 7 | 5 | 0 | 0 | 0 | 5 | 7 | 5 | 3 | 16 | YES |  |  |  | 247 | Yes | 2 | No | Monitor Raise to 212F (202 MVA)
304723,304726,1 | 115 | 304723 CAMDENJCT TT 115 304726 CAMDEN DUSTY 115 1 | Line | Camden - Camden Junction 115kV | 105.64 | 90.59 | 90.59 | 93.07 | [10 empty] | 92.79 |  |  |  |  | 100.86 | [5 empty] | 96.04 | [5 empty] | 91.95 | 91.7 | 94.33 | 91.29 | [11 empty] | 93.22 | 93.02 | 95.74 | 92.62 | 115.65 | 102.75 | 102.78 | 105.03 |  |  |  |  | 91.02 | [11 empty] | 90.99 | 91.64 | 91.44 | 93.95 | 91.39 | [84 empty] | 94.33 | 115.65 | 116.57 |  | 107 | 107 | 2 | 0 | 4 | 0 | 0 | 0 | 2 | 0 | 4 | 2 | 5 | NO |  |  | 179.83 | 284.45 | Yes | 2 | No | Wateree Cluster
304022,305009,1 | 230 | 304022 BRUN1 230 TT 230 305009 E1-DAWSCREEK 230 1 | Line | Brunswick Unit 1 - Barnard Creek 230kV | [7 empty] | 93.65 |  |  |  | 90.03 |  |  |  |  | 97.54 | [15 empty] | 92.72 | [9 empty] | 96.56 | [14 empty] | 92.36 | [17 empty] | 95.65 | 95.62 |  | 108.06 | 93.89 | 91.85 | 95.63 | 91.68 | 91.65 |  | 103.44 |  |  | 91.65 | 98.55 | 98.52 |  | 111.86 | 97.09 | 95.06 | 98.52 | [7 empty] | 94.1 | 94.06 |  | 106.12 | 92.08 |  |  |  | 101.31 |  |  |  | 96.65 | 96.62 |  | 109.73 | 95.02 | 92.92 | 96.63 | [8 empty] | 94.07 |  |  |  | 95.65 | [6 empty] | 91.74 | [6 empty] | 97.38 | [10 empty] | 108.06 | 111.86 | 86.94 | 110.73 | 637 | 637 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 2 | YES |  |  |  | 365.9 | Yes | 2 | Yes | Brunswick 1 – Barnard Creek 230kV line, Upgrade OOS relays, CT ratios, line trap, and line switches to allow use of 2806 A line conductor winter rating (1118 MVA) - ISD 7/13/2028
304614,304619,1 | 230 | 304614 BARNCRK W TT 230 304619 MASONBORO 230 1 | Line | Barnard Creek - Castle Hayne 230kV | [7 empty] | 92.36 | [8 empty] | 96.09 | [15 empty] | 91.43 | [9 empty] | 95.11 | [14 empty] | 91.08 | [17 empty] | 93.41 | 93.38 |  | 106.12 | 91.65 |  | 93.38 |  |  |  | 101.46 |  |  |  | 96.37 | 96.34 |  | 110.2 | 94.9 | 92.88 | 96.34 | [7 empty] | 91.89 | 91.85 |  | 104.2 |  |  |  |  | 99.41 |  |  |  | 94.58 | 94.55 |  | 108.16 | 92.92 | 90.71 | 94.56 | [8 empty] | 91.86 |  |  |  | 93.35 | [13 empty] | 94.96 | [10 empty] | 106.12 | 110.2 | 85.83 | 109.32 | 637 | 637 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 2 | 2 | YES |  |  |  | 365.9 | No | 2 | Yes | Barnard Creek – Castle Hayne 230kV line, Upgrade switches 38A-1, 38A-2 to 3000 A and 41B-3 to 2000 A (796 MVA) - ISD 3/31/2028
305169,305172,1 | 115 | 305169 LOUISBUR CAP 115 305172 E18-LOUISBRG 115 1 | Line | Franklinton - Spring Hope SS 115kV | 109.35 | 103.37 | 103.49 | 107.3 | 104.43 | [20 empty] | 102.48 | 96.57 | 96.7 | 100.57 | 97.65 | [20 empty] | 102.76 | 97.42 | 97.55 | 101.27 | 98.61 | [104 empty] | 0 | 109.35 | 97.16 |  | 201 | 201 | 5 | 2 | 2 | 0 | 0 | 0 | 5 | 2 | 2 | 3 | 9 | NO |  |  | 133.07 | 306.12 | Yes | 2 | No | Monitor - Reconductor with 1590 ACSR or equivalent (310 MVA) - Wood H-Frame
304726,304738,1 | 115 | 304726 CAMDEN DUSTY 115 304738 CAMD KENDAL 115 1 | Line | Camden - Camden Junction 115kV | 92.58 | [29 empty] | 99.4 | 103.38 | 103.14 | 105.93 | 102.33 |  |  |  | 91.5 | [6 empty] | 101.17 | 105.07 | 104.85 | 107.72 | 104 | 102.62 |  |  | 92.14 |  | 95.97 | 101.13 | 100.92 | 103.45 | 100.8 |  | 92.02 | 91.81 | 94.36 | 91.31 |  |  |  | 90.6 |  | 99.93 | 104.68 | 104.47 | 107.17 | 103.91 | [84 empty] | 105.93 | 107.72 | 103.37 |  | 107 | 107 | 0 | 9 | 9 | 0 | 0 | 0 | 0 | 9 | 9 | 2 | 9 | NO |  |  | 168.45 | 184.9 | Yes | 2 | No | Wateree Cluster
304088,304089,1 | 230 | 304088 HENDER 230TT 230 304089 HENDER 115TT 115 1 | Substation | Henderson 230kV | [103 empty] | 97.21 | 97.3 | 95.52 | 95.38 | 95.73 | [7 empty] | 100.94 | 101.03 | 99.68 | 99.55 | 100.07 | 97.87 | 101.04 | 92.13 | 92.21 | 91.02 | 90.9 | 91.21 |  | 92.22 | 93.66 | 97.31 | 96.9 | 96.99 | 95.57 | 95.43 | 95.69 | 93.79 | 97 | [7 empty] | 100.42 | 100.5 | 99.29 | 99.17 | 99.62 | 97.55 | 100.51 | 93.7 | 93.78 | 92.71 | 92.59 | 92.86 | 90.94 | 93.79 | 97.31 | 101.04 |  | 100.08 | 239 | 239 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 4 | 3 | 2 | 0 | YES |  |  |  | 252 | No | 2 | Yes | Henderson 230/115 kV Banks #1 & #2, Upgrade CT Ratios and Relay Settings (336 MVA) - ISD 12/1/2025
304261,304271,1 | 115 | 304261 LEESUB115STT 115 304271 FRNDSHIP TAP 115 1 | Line | Lee - Wallace 115kV | 105.3 |  |  | 103.23 | 97.36 | [14 empty] | 142.88 | 105.58 | 105.89 | 136.84 | 129.87 | [21 empty] | 122.07 |  |  | 115.72 | 111.9 | 92.72 |  |  | 90.84 | [16 empty] | 120.32 |  |  | 113.76 | 106.59 | [47 empty] | 93.2 | 93.07 |  |  |  |  | 93.1 | [30 empty] | 0 | 142.88 | 89.01 |  | 119 | 119 | 7 | 3 | 3 | 0 | 0 | 0 | 7 | 3 | 3 | 3 | 2 | NO |  |  | 130.92 |  | Yes | 1 | Yes | Asset Management has project to rebuild with larger conductor - 795 ACSS/TW
304208,304220,1 | 115 | 304208 ERWIN115 TT 115 304220 LILLINGTON 115 1 | Line | Cape Fear Plant - Erwin 115kV | 107.21 |  |  | 137.12 | 98.99 | [7 empty] | 99.22 |  |  |  |  | 99.8 |  | 106.57 |  |  | 133.16 | 95.45 |  | 104.38 |  |  | 131.4 | 93.82 |  |  |  | 102.78 |  |  |  |  | 104.59 |  |  |  |  | 110.78 |  | 114.62 | 91.75 | 92.08 | 140.79 | 102.69 |  |  |  | 113.64 |  |  |  |  | 95.17 |  |  |  |  | 99.04 |  | 91.64 |  |  | 114.28 |  | 114.12 | 93.34 | 93.54 | 138.81 | 101.06 | [84 empty] | 102.78 | 140.79 | 100.25 |  | 86 | 86 | 4 | 8 | 5 | 0 | 0 | 0 | 4 | 8 | 5 | 3 | 6 | NO |  |  |  | 87.4 | Yes | 1 | No | Monitor - Reconductor
304361,304362,1 | 230 | 304361 WESTEND230TT 230 304362 WESTENE115TT 115 1 | Substation | West End 230kV | [30 empty] | 96.61 | 97.16 | 97.16 | 96.66 | 96.78 | [5 empty] | 108.5 | 108.86 | 108.86 | 108.86 | 108.9 | 96.34 | 96.6 | 97.14 | 96.61 | 96.69 | [15 empty] | 97.92 | 98.76 | 98.76 | 98.71 | 98.91 | [33 empty] | 117.87 | 117.63 | 117.68 | 117.65 | 117.7 | 102.58 | 102.58 | 102.56 | 102.55 | 102.58 | 102.58 | 102.58 | 137.22 | 136.32 | 138.13 | 137.35 | 137.32 | 136.36 | 136.32 | 117.68 | 117.67 | 117.61 | 117.61 | 117.76 | 117.59 | 117.67 | 117.61 | 117.63 | [14 empty] | 102.23 | 102.22 | 103.69 | 103.73 | 101.28 | 103.98 | 102.22 | [7 empty] | 117.87 | 138.13 | 86.24 | 117.63 | 336 | 350 | 0 | 5 | 0 | 0 | 16 | 7 | 0 | 21 | 7 | 2 | 7 | YES |  |  |  |  | Yes | 1 | No | Radial serving load
304361,304363,2 | 230 | 304361 WESTEND230TT 230 304363 WESTENW115TT 115 2 | Substation | West End 230kV | [30 empty] | 96.37 | 97.2 | 97.2 | 96.65 | 96.78 | [5 empty] | 108.54 | 108.91 | 108.91 | 108.88 | 108.95 | 96.34 | 96.61 | 97.12 | 96.61 | 96.69 | [15 empty] | 97.96 | 98.81 | 98.81 | 98.76 | 98.96 | [33 empty] | 117.97 | 117.72 | 117.83 | 117.83 | 117.8 | 102.6 | 102.61 | 102.56 | 102.55 | 102.61 | 102.6 | 102.58 | 137.53 | 136.65 | 137.69 | 137.67 | 137.68 | 136.68 | 136.64 | 117.77 | 117.77 | 117.7 | 117.7 | 117.86 | 117.68 | 117.77 | 117.7 | 117.72 | [14 empty] | 102.3 | 102.3 | 103.76 | 103.8 | 101.29 | 104.06 | 102.3 | [7 empty] | 117.97 | 137.69 | 86.3 | 117.96 | 336 | 350 | 0 | 5 | 0 | 0 | 16 | 7 | 0 | 21 | 7 | 2 | 7 | YES |  |  |  |  | Yes | 1 | No | Radial serving load
304716,304725,1 | 115 | 304716 CAMDEN TAP 115 304725 CAMDEN115 TT 115 1 | Line | Camden - Camden Junction 115kV | [15 empty] | 90.1 |  | 92.98 |  |  |  |  | 90.95 | [7 empty] | 124.19 | 127.84 | 127.59 | 130.58 | 126.23 | 106.41 | 110.09 | 109.87 | 112.7 | 108.43 | 107 | 110.6 | 110.39 | 113.3 | 109.08 | 126.57 | 130.09 | 129.86 | 132.92 | 128.38 | [5 empty] | 122.43 | 126.77 | 126.55 | 129.33 | 125.72 | 109.44 | 113.75 | 113.53 | 116.27 | 112.47 | 109.55 | 114.22 | 114.01 | 116.8 | 113.26 | 127.36 | 131.29 | 131.08 | 134.02 | 129.8 | [81 empty] | 90.99 |  |  | 130.58 | 134.02 | 80.01 |  | 107 | 107 | 0 | 20 | 20 | 0 | 0 | 0 | 0 | 20 | 20 | 2 | 10 | NO |  |  | 149.01 |  | Yes | 1 | No | Wateree Cluster
304363,305106,1 | 115 | 304363 WESTENW115TT 115 305106 E14-EASTWOOD 115 1 | Line | West End - Southern Pines 115kV | [25 empty] | 91.1 | 91.87 | 91.9 | 91.96 | 91.66 | 101.86 | 102.75 | 102.75 | 100.53 | 100.27 | 93.89 | 94.53 | 94.54 | 94.56 | 94.57 | 115.35 | 115.85 | 115.86 | 115.94 | 115.81 | 100.19 | 100.46 | 102.79 | 100.51 | 100.53 | [15 empty] | 97.64 | 98.9 | 98.91 | 98.9 | 99.13 | [33 empty] | 107.38 | 106.89 | 107.18 | 107.19 | 107.17 | 91.22 | 91.23 | 90.95 | 90.94 | 91.18 | 91.18 | 91.17 | 130.44 | 128.88 | 131.71 | 130.78 | 131.11 | 128.88 | 128.87 | 107.09 | 107.06 | 106.82 | 106.8 | 107.28 | 106.74 | 107.05 | 106.8 | 106.88 | [28 empty] | 107.38 | 131.71 | 91.04 | 107.34 | 239 | 239 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 31 | 0 | 1 | 12 | YES |  |  |  |  | Yes | 1 | No | Radial serving load
304716,304724,1 | 115 | 304716 CAMDEN TAP 115 304724 CAMD DEKALB 115 1 | Line | Camden - Camden Junction 115kV | [30 empty] | 115.05 | 118.79 | 118.55 | 121.49 | 117.33 | 98.56 | 102.3 | 102.08 | 104.88 | 100.76 | 97.65 | 101.29 | 101.08 | 103.94 | 99.93 | 117.27 | 120.9 | 120.68 | 123.68 | 119.35 | [5 empty] | 112.84 | 117.41 | 117.19 | 119.92 | 116.55 | 101.38 | 105.8 | 105.58 | 108.27 | 104.66 | 99.47 | 104.35 | 104.14 | 106.86 | 103.59 | 117.57 | 121.73 | 121.52 | 124.4 | 120.43 | [84 empty] | 121.49 | 124.4 | 87.91 |  | 107 | 107 | 0 | 17 | 19 | 0 | 0 | 0 | 0 | 17 | 19 | 2 | 10 | NO |  |  | 155.4 |  | Yes | 1 | No | Wateree Cluster
304724,304738,1 | 115 | 304724 CAMD DEKALB 115 304738 CAMD KENDAL 115 1 | Line | Camden - Camden Junction 115kV | [30 empty] | 102.01 | 105.93 | 105.69 | 108.53 | 104.76 |  | 91.38 | 91.16 | 93.87 | 90.08 |  |  |  | 91.22 |  | 103.92 | 107.75 | 107.53 | 110.44 | 106.54 | 99.67 |  |  |  |  | 98.94 | 103.93 | 103.72 | 106.32 | 103.45 |  | 94.52 | 94.3 | 96.91 | 93.67 |  | 90.6 | 90.4 | 92.95 | 90.28 | 103.17 | 107.75 | 107.54 | 110.29 | 106.82 | [84 empty] | 108.53 | 110.44 | 100.27 |  | 107 | 107 | 0 | 10 | 9 | 0 | 0 | 0 | 0 | 10 | 9 | 2 | 9 | NO |  |  | 165.39 |  | Yes | 1 | No | Wateree Cluster
305173,305176,1 | 115 | 305173 E18-POCOMOKE 115 305176 E18-YOUNGSVL 115 1 | Line | Falls - Franklinton 115kV West | 91.09 | 93.23 | 93.29 | 98.06 | 92.26 | [20 empty] | 98.03 | 100.08 | 100.11 | 104.95 | 98.92 | [20 empty] | 95.58 | 98.14 | 98.18 | 102.78 | 96.97 | [104 empty] | 0 | 104.95 | 100.52 |  | 170 | 170 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 3 | 1 | 2 | 4 | NO |  |  |  | 233.5 | Yes | 1 | No | Monitor - Raise to 212F (202 MVA)
304096,304105,1 | 115 | 304096 YOUNGSVILLE 115 304105 FRANKLIN TT 115 1 | Line | Falls - Franklinton 115kV East | 91.74 | 93.38 | 93.44 | 97.56 | 92.64 | [20 empty] | 97.66 | 99.2 | 99.24 | 103.51 | 98.31 |  |  |  | 90.48 | [9 empty] | 93.22 | [6 empty] | 95.52 | 97.55 | 97.6 | 101.6 | 96.63 | [104 empty] | 90.48 | 103.51 | 99.57 |  | 200 | 200 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | YES |  |  |  |  | Yes | 1 | No | Monitor - Reconductor
304619,304626,1 | 230 | 304619 MASONBORO 230 304626 WRIGHTSVILLE 230 1 | Line | Barnard Creek - Castle Hayne 230kV | [78 empty] | 95.84 | [6 empty] | 92.41 | [6 empty] | 98.59 | [13 empty] | 93.92 |  |  |  |  | 90.34 | [6 empty] | 96.53 | [40 empty] | 95.84 | 98.59 |  | 98.89 | 637 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES |  |  |  |  | Below 100% | 1 | Yes | Barnard Creek – Castle Hayne 230kV line, Upgrade switches 38A-1, 38A-2 to 3000 A and 41B-3 to 2000 A (796 MVA) - ISD 3/31/2028
304781,304780,1 | 230 | 304781 CANERV230 TT 230 304780 CANERV115STT 115 1 | Substation | Cane River 230kV | [75 empty] | 93.56 | 93.58 | 93.56 | 93.56 | 93.56 | 93.56 | 93.99 | [7 empty] | 104.86 | 104.48 | 104.87 | 104.87 | 104.87 | 104.87 | 105.24 | 93.56 | 93.66 | 93.58 | 93.58 | 93.58 | 93.56 | 93.99 | 93.56 | 93.64 | 93.56 | 93.56 | 93.56 | [7 empty] | 104.87 | 104.48 | 104.87 | 104.87 | 104.87 | 104.88 | 105.25 | 93.56 | 93.64 | 93.56 | 93.56 | 93.58 | 93.56 | 93.99 | 93.58 | 93.99 | 93.56 | 93.64 | 93.56 | 93.56 | 93.56 | 93.58 | 93.99 | [7 empty] | 104.87 | 104.48 | 104.87 | 104.87 | 104.87 | 104.89 | 105.24 | 93.58 | 93.63 | 93.56 | 93.56 | 93.56 | 93.56 | 93.99 | 93.99 | 105.25 |  | 104.87 | 239 | 239 | 0 | 0 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 3 | 0 | YES |  |  |  |  | Yes | 1 | Yes | Cane River 230/115 kV transformer, upgrade CT ratios and relays settings (336 MVA) - ISD 12/1/2028
900009,900017,1 | 230 | 900009 ID_565080 230 900017 ID_566488 230 1 | Line | Robinson Plant - Rockingham 230kV |  | 97.6 | 96.71 | 103.09 |  |  | 94.57 | 93.73 | 99.78 | 92.11 | 99.64 | 98.79 | 104.91 |  |  | 90.53 |  | 95.7 |  | 90.35 | 98.08 | 97.24 | 104.13 | [10 empty] | 91.99 | [125 empty] | 99.78 | 104.91 | 110.75 |  | 540 | 540 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | NO |  |  | 126.36 |  | Yes | 1 | No | Monitor - Finish 29 mile rebuild to 6-1590 MCM ACSR (1195 MVA)
304018,900009,1 | 230 | 304018 ROB2 230 TT 230 900009 ID_565080 230 1 | Line | Robinson Plant - Rockingham 230kV | [8 empty] | 93.32 |  | 93.25 | 92.4 | 98.54 | [7 empty] | 91.66 | 90.82 | 97.72 | [136 empty] | 93.32 | 98.54 | 97.78 |  | 540 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  | 113.17 |  | Below 100% | 1 | No | Monitor - Finish 29 mile rebuild to 6-1590 MCM ACSR (1195 MVA)
304575,304587,1 | 115 | 304575 LAKE WACCA 115 304587 DELCO115W TT 115 1 | Line | Delco - Whiteville 115kV | [19 empty] | 162.98 | 100.08 | 95.82 | 141.69 | 146.35 |  | 93.95 | [19 empty] | 170.5 | 106.09 | 101.96 | 148.35 | 152.36 | 111.12 |  |  | 95.37 | 102.28 | [10 empty] | 100.48 |  |  |  |  | 194.3 | 126.46 | 122.36 | 170.9 | 174.7 | [21 empty] | 108.3 | 108.53 |  |  | 93.45 | 98.1 | 108.5 | [19 empty] | 114 | 114.23 |  |  | 97.88 | 101.87 | 114.2 | [23 empty] | 120.81 | 121.04 |  |  | 105.42 | 109.77 | 121 | 0 | 194.3 |  | 81.18 | 228 | 228 | 4 | 5 | 8 | 3 | 4 | 5 | 7 | 9 | 13 | 3 | 2 | NO |  |  |  |  | Yes | 0 | No | Monitor - Rebuild 16.86 miles
304271,304273,1 | 115 | 304271 FRNDSHIP TAP 115 304273 KORNEGAY SUB 115 1 | Line | Lee - Wallace 115kV | 110.77 |  |  | 108.63 | 102.75 | [14 empty] | 148.57 | 111.22 | 111.54 | 142.45 | 135.45 | [21 empty] | 127.47 | 92.75 | 93.05 | 121.01 | 116.95 | 98.19 |  |  | 96.26 | 90.25 | [15 empty] | 126.14 |  |  | 119.49 | 112.19 | [47 empty] | 97.65 | 97.52 |  |  | 93.08 |  | 97.54 | [30 empty] | 0 | 148.57 | 94.36 |  | 119 | 119 | 8 | 3 | 3 | 0 | 0 | 0 | 8 | 3 | 3 | 3 | 3 | NO |  |  |  |  | Yes | 0 | Yes | Asset Management has project to rebuild with larger conductor - 795 ACSS/TW
304258,305126,1 | 115 | 304258 CLINTON NTH 115 305126 E15-CLINTON 115 1 | Line | Clinton - Vander 115kV | 93.69 | [18 empty] | 105.47 |  |  | 96.14 | 94.6 |  | 94.37 | [19 empty] | 108.79 |  |  | 99.08 | 97.28 | 100.64 |  |  | 93.58 | 93.31 | [15 empty] | 135.95 | 106.08 | 106.34 | 124.42 | 122.37 | [84 empty] | 0 | 135.95 |  |  | 163 | 163 | 1 | 1 | 6 | 0 | 0 | 0 | 1 | 1 | 6 | 3 | 1 | NO |  |  |  |  | Yes | 0 | No | Monitor - Rebuild 0.91 miles
304730,304725,1 | 230 | 304730 CAMDEN230 TT 230 304725 CAMDEN115 TT 115 1 | Substation | Camden 230kV | [19 empty] | 92.81 |  |  | 92.16 |  |  | 90.1 |  |  |  |  | 106.76 | 103.57 | 103.44 | 106.47 | 95.33 | 95.75 | 92.4 | 92.25 | 95.18 | [6 empty] | 114.39 | 111.49 | 111.34 | 114.28 | 103.13 | 98.91 | 96.47 | 96.35 | 99.23 |  | 115.42 | 113.22 | 113.09 | 115.83 | 105.5 | 108.13 | 105.77 | 105.64 | 108.4 | 97.8 | 104.73 | 102.84 | 102.72 | 105.47 | 95.1 | 123.8 | 121.94 | 121.8 | 124.46 | 114.07 | [77 empty] | 93.88 | 93.16 | 91.69 | 91.55 | 94.54 |  | 93.07 | 115.83 | 124.46 |  |  | 224 | 224 | 0 | 9 | 18 | 0 | 0 | 0 | 0 | 9 | 18 | 2 | 9 | NO |  |  |  |  | Yes | 0 | No | Wateree Cluster
305034,305330,1 | 230 | 305034 E4-POWELL 230 305330 BLADENSOLTAP 230 1 | Line | Cumberland - Whiteville 230kV | 99.95 |  |  | 101.71 | 90.52 | [14 empty] | 121.12 | 95.81 |  | 120.59 | 108.6 | [21 empty] | 111.04 |  |  | 110.28 | 97.72 | [20 empty] | 108.38 |  |  | 107.22 | 95.27 | [84 empty] | 0 | 121.12 | 82.17 |  | 475 | 475 | 4 | 2 | 2 | 0 | 0 | 0 | 4 | 2 | 2 | 3 | 1 | NO |  |  |  |  | Yes | 0 | No | Monitor - Raise or Reconductor 1.71 miles
304035,304557,1 | 115 | 304035 SUTTON115 TT 115 304557 WILM GNF 115 1 | Line | Sutton Plant - Wilmington GNF 115kV | 100.6 | 99.92 | 101.12 | 100.42 | 100.41 | 100.72 | 99.72 | 99.95 | 100.67 | 100.46 | 100.46 | 100.91 | 100.38 | 100.34 | 100.67 | 100.12 | 100.05 | 100.64 | 100.6 | 102.96 | 99.67 | 99.61 | 106.37 | 105.27 | 100.64 | 99.49 | 99.71 | 99.96 | 99.34 | 99.31 | 100.79 | 99.79 | 100.02 | 100.76 | 100.69 | 100.49 | 100.53 | 100.97 | 100.4 | 100.36 | 99.8 | 100.21 | 100.29 | 99.78 | 99.73 | 103.32 | 99.61 | 101.55 | 106.72 | 105.58 | 100.02 | 99.89 | 100.23 | 99.52 | 99.51 | 100.47 | 100.88 | 100.14 | 100.37 | 100.35 | 100.14 | 100.6 | 100.56 | 100.02 | 100 | 99.5 | 99.54 | 99.55 | 99.49 | 99.49 | 106.69 | 102.41 | 102.81 | 102.65 | 108.41 | [84 empty] | 100.88 | 108.41 | 100.75 |  | 25.3 | 25.3 | 20 | 15 | 16 | 0 | 0 | 0 | 20 | 15 | 16 | 3 | 17 | NO |  |  |  |  | Yes | 0 | Yes | (Non-BES) Raise the conductor or other solution
304052,304220,1 | 115 | 304052 CAPEFR115STT 115 304220 LILLINGTON 115 1 | Line | Cape Fear Plant - Erwin 115kV |  |  |  | 110.02 | [18 empty] | 96.16 | [5 empty] | 102.11 | [19 empty] | 100.04 | [24 empty] | 100.32 | [85 empty] | 0 | 110.02 |  | 105.33 | 107 | 107 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 3 | 2 | NO |  |  |  |  | Yes | 0 | No | Monitor - Reconductor
Note on GE3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is overload > major component rating?