## Base Reliability
Season | Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | Contingency Rating (MVA) | Contingency Flow (MVA) | Final AC % Loading | Major Component Limited | Previous Project | Solution
30w | BEL1GM | PARKWOOD_EHV | 306848 | 6PL GRDN 230.00 | 306850 | 8PL GRDN 500.00 | 5 | 1519 | 1533.8 | 101 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | BEL1GM | PARKWOOD_EHV | 306848 | 6PL GRDN 230.00 | 306850 | 8PL GRDN 500.00 | 5 | 1519 | 1524.3 | 100.3 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | PLGDNGLRVN_B | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 132 | 153.9 | 124.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | PLGDNGLRVN_B | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 159 | 155.2 | 105 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | PLGDNGLRVN_B | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 132 | 157.9 | 128.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | PLGDNGLRVN_B | 306834 | MILLISTB 100.00 | 306935 | LINDENST 100.00 | 1 | 159 | 158.1 | 107.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | PLGDNGLRVN_B | 306899 | GLENOLAT 100.00 | 306955 | RNDLMN T 100.00 | 1 | 166 | 145.3 | 99.1 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | PLGDNGLRVN_B | 306899 | GLENOLAT 100.00 | 306955 | RNDLMN T 100.00 | 1 | 166 | 148.6 | 102.6 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | LNDNRNDLMN_W_FS | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 239.4 | 130.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | SHPVGM | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 238.5 | 129.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 228.1 | 123.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | LNDNRNDLMN_W_FS | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 261.2 | 127 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | BUCCGM | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 251.4 | 121.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 245 | 118.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | LNDNRNDLMN_W_FS | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 244.5 | 134.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | SHPVGM | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 243 | 132.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 183 | 233 | 127.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | LNDNRNDLMN_W_FS | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 269.2 | 131.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | BUCCGM | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 257.8 | 124.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | RANDLEMANW | 306949 | PL GARDN 100.00 | 309892 | DUK 309892 100.00 | 1 | 207 | 252.1 | 122.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | PLGARDEN_YB | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 132 | 130.3 | 103 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | PLGDNSWPVL_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 132 | 130.2 | 102.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | PLGARDEN_YB | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 159 | 148.7 | 99.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | PLGDNGLRVN_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 159 | 148.6 | 99.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | PLGARDEN_YB | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 132 | 132.7 | 105.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | PLGDNGLRVN_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 132 | 132.6 | 105.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | PLGARDEN_YB | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 159 | 151.1 | 101.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | PLGDNGLRVN_W | 306935 | LINDENST 100.00 | 306942 | MILLIS 100.00 | 1 | 159 | 151 | 101.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | SHPVGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 244.7 | 133.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 236.2 | 130.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 233.6 | 127.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 253.8 | 125.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 256.1 | 124 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30w | STUDY | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 249.2 | 120.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | SHPVGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 249.3 | 136.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 241.8 | 134.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 183 | 238.6 | 130.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | PLGDNRDLMN_B | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 262.7 | 130 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | BUCCGM | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 262.9 | 127.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35w | STUDY | RANDLEMANBL | 306949 | PL GARDN 100.00 | 309893 | DUK 309893 100.00 | 1 | 207 | 256.7 | 124.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | ALBSGM | BELMONTW_FS | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 114.7 | 98 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | BELMONTW_FS | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 114.6 | 96.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | BTCLUB_GARLNDWH | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 114.6 | 96.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | ALBSGM | BELMONTW_FS | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 120.5 | 103 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | BELMONTW_FS | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 120.4 | 101.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
35s | STUDY | BTCLUB_GARLNDWH | 308865 | LTLROKTO 100.00 | 309959 | BT CLUB R 100.00 | 1 | 120 | 120.4 | 101.5 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2027
30s | STUDY | CAMPCLFSDBL | 307452 | DUK 307452 44.00 | 307558 | 1RUEMC 7 44.000 | 1 | 24.8 | 27.7 | 106.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | CAMPCLFSDBL | 307452 | DUK 307452 44.00 | 307558 | 1RUEMC 7 44.000 | 1 | 24.8 | 26.9 | 103.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_RB | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 24.8 | 43.8 | 187 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 24.8 | 43.8 | 187 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | TUXDGM | HENDBK3 | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 22.2 | 22.6 | 99 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 32.2 | 56 | 202.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 32.2 | 56 | 202.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDNVLECHO_W | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 24.8 | 46.6 | 201.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | TUXDGM | HENDBK3 | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 22.2 | 23.1 | 101.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307304 | 1LANDRUM 44.000 | 1 | 32.2 | 57.9 | 210.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_RB | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 28.9 | 127.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_HT | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 28.9 | 127.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 38.6 | 151.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 38.6 | 151.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDNVLECHO_W | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 30.8 | 138.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_RB | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 39.6 | 157.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307304 | 1LANDRUM 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 39.6 | 157.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 307344 | 1SALUDAA 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 30.5 | 24.2 | 118.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307344 | 1SALUDAA 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 30.5 | 24.2 | 118.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_RB | 307344 | 1SALUDAA 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 30.5 | 24.9 | 123.1 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307344 | 1SALUDAA 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 30.5 | 24.9 | 123.1 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_RB | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 28.9 | 127.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDNVLECHO_W | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 28.9 | 127.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 37.1 | 152 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 37.1 | 152 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDNVLECHO_W | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 24.8 | 30.2 | 138.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_RB | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 38.1 | 157.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 308582 | 1TRYONA 44.000 | 308583 | DUK 308583 44.00 | 1 | 32.2 | 38.1 | 157.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_RB | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 24.8 | 36.3 | 160.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 24.8 | 36.3 | 160.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 32.2 | 46.5 | 184 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDNVLECHO_W | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 24.8 | 38.5 | 173.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_RB | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 32.2 | 47.9 | 191.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307246 | 1CAMPOBL 44.000 | 307343 | DUK 307343 44.00 | 1 | 32.2 | 48 | 191.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_RB | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 24.8 | 36.2 | 160.1 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HNDRSNVL_HT | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 24.8 | 36.2 | 160 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 32.2 | 44.5 | 184.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 32.2 | 44.5 | 184.3 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDNVLECHO_W | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 24.8 | 37.6 | 173.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307343 | DUK 307343 44.00 | 307598 | 1TRYONB 44.000 | 1 | 32.2 | 45.8 | 191.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_RB | 307355 | 1TUXEDO 44.000 | 307553 | 1SALUDAB 44.000 | 1 | 30.5 | 27.2 | 133.7 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | STUDY | HNDRSNVL_HT | 307355 | 1TUXEDO 44.000 | 307553 | 1SALUDAB 44.000 | 1 | 30.5 | 27.2 | 133.6 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HNDRSNVL_HT | 307355 | 1TUXEDO 44.000 | 307553 | 1SALUDAB 44.000 | 1 | 30.5 | 26.4 | 100 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_RB | 307355 | 1TUXEDO 44.000 | 307553 | 1SALUDAB 44.000 | 1 | 30.5 | 28.1 | 138.9 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | HNDRSNVL_HT | 307355 | 1TUXEDO 44.000 | 307553 | 1SALUDAB 44.000 | 1 | 30.5 | 28.1 | 138.8 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | LECCGM | AB_SHADBK2_L | 308622 | LEE CC 100.00 | 309811 | FIVECRCLPV 100.00 | 1 | 96 | 115.9 | 116.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDYLECCGC | BASE CASE | 308622 | LEE CC 100.00 | 309811 | FIVECRCLPV 100.00 | 1 | 96 | 108.1 | 108.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | LEEC_YB_NOGC | 308622 | LEE CC 100.00 | 309811 | FIVECRCLPV 100.00 | 1 | 105 | 114.4 | 104.2 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | CAT1GM | NEWPORT_UGBL_TC | 306375 | GT FALL1 100.00 | 309837 | RANGERLN 100.00 | 2 | 116 | 123.5 | 104.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDYRICHVRS | EARLW-SHEL_P21 | 306377 | HILLTOP 100.00 | 308545 | DUK 308545 100.00 | 1 | 211 | 208.9 | 99 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | SHLBYDHILL_W | 306377 | HILLTOP 100.00 | 308545 | DUK 308545 100.00 | 1 | 211 | 202.3 | 95.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30s | STUDY | HB230HT2_FS | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 3 | 492 | 469.7 | 96.3 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HB230HT2_FS | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 3 | 492 | 516.4 | 105.3 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | GRBTGM | MECKLENBURGW | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 3 | 492 | 474.5 | 97 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | HB230HT4_FS | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 4 | 492 | 495.4 | 100.9 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | GRBTGM | MECKLENBURGB | 306538 | 6HARRISB 230.00 | 306540 | 6MCGUIRE 230.00 | 4 | 492 | 474.5 | 97 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2028
30w | 99ISGM | GAFFNEY2 | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 1 | 41.9 | 42.7 | 101.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
30w | STUDY | BLCKSBRG_BUS | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 1 | 41.9 | 41 | 97.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35w | STUDY | BLCKSBRG_BUS | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 1 | 41.9 | 42.9 | 102.4 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35w | 99ISGM | GAFFNEY2 | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 1 | 41.9 | 42.7 | 101.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
30w | 99ISGM | GAFFNEY1 | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 2 | 41.5 | 40.4 | 97.3 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35w | 99ISGM | GAFFNEY1 | 306254 | GAFFNEY 100.00 | 307465 | 1GAFFNEY 44.000 | 2 | 41.5 | 40.5 | 97.5 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35s | CAT1GM | STEMMONSWN_FS | 306543 | 6RIVRBENR 230.00 | 309836 | MCSTEM2 230.00 | 1 | 557 | 535.5 | 96.5 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35s | CAT1GM | STEMMONSBN_FS | 308543 | 6RIVRBENY 230.00 | 309836 | MCSTEM2 230.00 | 2 | 557 | 535.9 | 96.6 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2029
35s | CAT1GM | RCHMNDWRCTR_EHV | 306333 | 6NEWPORT 230.00 | 306337 | 8NEWPORT 500.00 | A5 | 1120 | 1117 | 99.7 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2031
30w | STUDY | HNDRSNVL_RB | 307283 | 1HNDRSNV 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 60 | 46 | 119.9 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2032
30w | STUDY | HNDRSNVL_HT | 307283 | 1HNDRSNV 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 60 | 46 | 119.9 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2032
35s | STUDY | HNDRSNVL_HT | 307283 | 1HNDRSNV 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 59 | 49.4 | 97.4 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2032
35w | STUDY | HNDRSNVL_RB | 307283 | 1HNDRSNV 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 60 | 47.4 | 123.8 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2032
35w | STUDY | HNDRSNVL_HT | 307283 | 1HNDRSNV 44.000 | 307355 | 1TUXEDO 44.000 | 1 | 60 | 47.4 | 123.8 | No |  | Asset Management / Generator Interconnection project will address. Planned for 2032
35w | TUXDGM | BASE CASE | 307214 | DUK 307214 44.00 | 307256 | DUK 307256 44.00 | 1 | 38.4 | 36.1 | 96.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDYLECCGC | BASE CASE | 307214 | DUK 307214 44.00 | 307256 | DUK 307256 44.00 | 1 | 38.4 | 36.1 | 96.9 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35w | STUDY | BASE CASE | 307214 | DUK 307214 44.00 | 307256 | DUK 307256 44.00 | 1 | 38.4 | 36.1 | 96.8 | Yes |  | Asset Management / Generator Interconnection project will address. Planned for 2028
35s | STUDY | LKWDOAKLWN_B | 306611 | LAKEWOOD 100.00 | 306695 | BUCKEYET 100.00 | 1 | 202 | 198.3 | 97 | Yes |  | Continue to monitor, consider submitting a project
35s | STUDYRICHVRS | ELZBTHBS-WL_P21 | 306584 | ELIZBETH 100.00 | 306631 | N CHARLT 100.00 | 1 | 208 | 195.9 | 95.8 | Yes |  | Continue to monitor, consider submitting a project
35s | STUDY | WOODLWN_LT6R | 306584 | ELIZBETH 100.00 | 306631 | N CHARLT 100.00 | 1 | 208 | 195.9 | 95.6 | Yes |  | Continue to monitor, consider submitting a project
35s | BEL1GM | BANNERTOWNB | 306763 | MITCHL R 100.00 | 306835 | SRYYDKN7 100.00 | 1 | 93 | 92.2 | 96.3 | No |  | Continue to monitor, consider submitting a project
35s | STUDY | ENOBRAGTWN_W | 306881 | ENO 100.00 | 306916 | HORTON R 100.00 | 1 | 120 | 117.7 | 95.7 | No |  | Continue to monitor, consider submitting a project
35s | STUDY | ENO_RB | 306881 | ENO 100.00 | 308630 | HORTON TW 100.00 | 1 | 120 | 116.5 | 95.8 | No |  | Continue to monitor, consider submitting a project
35s | STUDY | PEACHVY_YB | 306269 | LAWSONFK 100.00 | 306287 | PEACH VY 100.00 | 1 | 166 | 160.5 | 96.3 | No |  | Continue to monitor, consider submitting a project
30w | STUDYRICHVRS | TIGERB | 306198 | TIGER 100.00 | 306271 | LELIA TP 100.00 | 1 | 138 | 134.8 | 95.8 | No |  | Continue to monitor, consider submitting a project
30s | STUDYRICHVRS | CLEARCKB-HB_P21 | 306630 | MORN STR 100.00 | 306677 | UNEMC11B 100.00 | 1 | 132 | 125.5 | 96.1 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
30s | STUDY | HARSBRG_LT4R_CS | 306630 | MORN STR 100.00 | 306677 | UNEMC11B 100.00 | 1 | 132 | 125.5 | 96 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
35s | STUDYRICHVRS | CLEARCKB-HB_P21 | 306630 | MORN STR 100.00 | 306677 | UNEMC11B 100.00 | 1 | 132 | 131.3 | 100.7 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
35s | STUDY | HARSBRG_LT4R_FS | 306630 | MORN STR 100.00 | 306677 | UNEMC11B 100.00 | 1 | 132 | 131.3 | 100.6 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
30s | STUDYRICHVRS | CLEARCKB-HB_P21 | 306677 | UNEMC11B 100.00 | 306686 | WILGROVE 100.00 | 1 | 132 | 123.6 | 96.1 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
30s | STUDY | HARSBRG_LT4R_CS | 306677 | UNEMC11B 100.00 | 306686 | WILGROVE 100.00 | 1 | 132 | 123.7 | 96 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
35s | STUDYRICHVRS | CLEARCKB-HB_P21 | 306677 | UNEMC11B 100.00 | 306686 | WILGROVE 100.00 | 1 | 132 | 129.3 | 100.8 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
35s | STUDY | HARSBRG_LT4R_FS | 306677 | UNEMC11B 100.00 | 306686 | WILGROVE 100.00 | 1 | 132 | 129.3 | 100.7 | Yes |  | CTPCDEC03 (New Project) - correct clearance issues to get full line rating
30w | STUDYRICHVRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 97.3 | 102.7 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
30w | STUDY | PACOLET_LT2Y | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 97.5 | 102.7 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
35w | STUDYSCPSVRS | GLENSPW-PAC_P21 | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 100.1 | 106 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
35w | STUDY | PACOLET_LT2Y | 306310 | WOODRUFF 100.00 | 308478 | LAUEC36 100.00 | 1 | 103 | 100.1 | 105.9 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
30w | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 90.8 | 96.9 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
35w | STUDY | PACOLET_LT2R | 306160 | LAUEC39 100.00 | 306310 | WOODRUFF 100.00 | 1 | 103 | 93.2 | 99.9 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
35s | STUDYLOOKGC | LOOKOUT_RB | 306465 | HICKORY 100.00 | 306496 | SWETWATT 100.00 | 1 | 166 | 159.7 | 95.2 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
35s | STUDYLOOKGC | LKOUTBUEL_W | 306465 | HICKORY 100.00 | 306496 | SWETWATT 100.00 | 1 | 166 | 159.7 | 95.2 | No |  | CTPCDEC04 (New Project) - Upgrade Ancillary Equipment to increase rating
30w | STUDY | LKEMORY_BUS1 | 308482 | 5LAKEMRY 161.00 | 308595 | 2LAKEMYA 66.000 | 3 | 82 | 111.3 | 135.8 | Yes |  | CTPCDEC05 (New Project) - Add capacitor banks at Lake Emory
35w | STUDY | LKEMORY_BUS1 | 308482 | 5LAKEMRY 161.00 | 308595 | 2LAKEMYA 66.000 | 3 | 82 | 119.1 | 145.3 | Yes |  | CTPCDEC05 (New Project) - Add capacitor banks at Lake Emory
35s | AMPVGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 244.4 | 95.5 | No |  | Limited by a relay settings. No project needed to address
35w | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 270.9 | 106.1 | No |  | Limited by a relay settings. No project needed to address
35w | STUDY | STAMYMKSVL_W | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 259.7 | 101.8 | No |  | Limited by a relay settings. No project needed to address
35w | STUDY | BEULAHW | 306454 | ENRG U18 100.00 | 306490 | STAMEY 100.00 | 1 | 249 | 255.3 | 100 | No |  | Limited by a relay settings. No project needed to address
35s | AMPVGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 244.4 | 95.5 | No |  | Limited by a relay settings. No project needed to address
35w | LOOKGM | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 270.9 | 106.1 | No |  | Limited by a relay settings. No project needed to address
35w | STUDY | STAMYBEULH_B | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 262.5 | 103.6 | No |  | Limited by a relay settings. No project needed to address
35w | STUDY | BEULAHB | 306490 | STAMEY 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 249 | 255.3 | 100 | No |  | Limited by a relay settings. No project needed to address
30w | STUDY | CHESNBK3 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 2 | 27 | 26.9 | 99.6 | Yes |  | Local Load, continue to monitor and consider future project
30w | WYLIGM | CHESNBK3 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 2 | 27 | 26.9 | 99.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYRICHVRS | CHESNBK3 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 2 | 27 | 27.9 | 103.3 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | CHESNBK3 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 2 | 27 | 27.9 | 103.2 | Yes |  | Local Load, continue to monitor and consider future project
30w | CLI5GM | CHESNBK2 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 3 | 27 | 26.9 | 99.7 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | CHESNBK2 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 3 | 27 | 26.9 | 99.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | CLI5GM | CHESNBK2 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 3 | 27 | 27.9 | 103.4 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | CHESNBK2 | 307425 | 1CHESNEE 44.000 | 309320 | CHESNEE2 100.00 | 3 | 27 | 27.9 | 103.3 | Yes |  | Local Load, continue to monitor and consider future project
30s | STUDY | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 37.7 | 37.2 | 98.8 | No |  | Local Load, continue to monitor and consider future project
30s | WYLIGM | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 37.7 | 37.2 | 98.8 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 37.7 | 38.6 | 102.5 | No |  | Local Load, continue to monitor and consider future project
35s | WYLIGM | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 37.7 | 38.6 | 102.5 | No |  | Local Load, continue to monitor and consider future project
35w | STUDYSCPSVRS | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 42.1 | 40.5 | 96.2 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 2 | 42.1 | 40.5 | 96.1 | Yes |  | Local Load, continue to monitor and consider future project
35s | THALGM | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 3 | 37.7 | 36.3 | 96.4 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | CORONBK4 | 306028 | CORONACA 100.00 | 307049 | 1CORONAC 44.000 | 3 | 37.7 | 36.3 | 96.3 | No |  | Local Load, continue to monitor and consider future project
30w | CLI6GM | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 1 | 24.8 | 24.7 | 99.8 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 1 | 24.8 | 24.7 | 99.5 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYLEECVRS | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 1 | 24.8 | 25.7 | 103.8 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 1 | 24.8 | 25.7 | 103.6 | Yes |  | Local Load, continue to monitor and consider future project
30w | MCG1GM | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 2 | 24.8 | 24.6 | 99.1 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 2 | 24.8 | 24.5 | 98.8 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYLEECVRS | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 2 | 24.8 | 25.6 | 103.1 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 2 | 24.8 | 25.5 | 102.9 | Yes |  | Local Load, continue to monitor and consider future project
30w | CLI6GM | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 3 | 24.8 | 24.7 | 99.8 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 3 | 24.8 | 24.7 | 99.5 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYLEECVRS | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 3 | 24.8 | 25.7 | 103.8 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | MEBANE4 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 3 | 24.8 | 25.7 | 103.6 | Yes |  | Local Load, continue to monitor and consider future project
30w | RHM1GM | MEBANE3 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 4 | 26.2 | 25.1 | 95.9 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | MEBANE3 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 4 | 26.2 | 25.1 | 95.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYLEECVRS | MEBANE1 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 4 | 26.2 | 26.1 | 99.8 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | MEBANE3 | 308433 | 1MEBANE 44.000 | 309368 | MEBANE2 100.00 | 4 | 26.2 | 26.1 | 99.6 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | MOCKS6 | 308173 | 1MOCKSVL 44.000 | 309354 | MOCKSVL2 100.00 | 4 | 38.1 | 40 | 104.9 | No |  | Local Load, continue to monitor and consider future project
30w | STUDYWATRVRS | MOCKS6 | 308173 | 1MOCKSVL 44.000 | 309354 | MOCKSVL2 100.00 | 4 | 38.1 | 40 | 104.9 | No |  | Local Load, continue to monitor and consider future project
35w | STUDY | MOCKS6 | 308173 | 1MOCKSVL 44.000 | 309354 | MOCKSVL2 100.00 | 4 | 38.1 | 41.5 | 109 | No |  | Local Load, continue to monitor and consider future project
35w | STUDYWATRVRS | MOCKS6 | 308173 | 1MOCKSVL 44.000 | 309354 | MOCKSVL2 100.00 | 4 | 38.1 | 41.5 | 109 | No |  | Local Load, continue to monitor and consider future project
30s | LECCGM | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 24 | 104.9 | No |  | Local Load, continue to monitor and consider future project
30s | STUDY | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 24 | 104.6 | No |  | Local Load, continue to monitor and consider future project
30w | LECCGM | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 22.6 | 98.8 | No |  | Local Load, continue to monitor and consider future project
30w | STUDY | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 22.6 | 98.7 | No |  | Local Load, continue to monitor and consider future project
35s | LECCGM | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 25.1 | 109.5 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 25 | 109.3 | No |  | Local Load, continue to monitor and consider future project
35w | LECCGM | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 23.4 | 102.2 | No |  | Local Load, continue to monitor and consider future project
35w | STUDY | OAKVALE1 | 307328 | 1OAKVALE 44.000 | 309315 | OAKVALE2 100.00 | 2 | 22.9 | 23.4 | 102.1 | No |  | Local Load, continue to monitor and consider future project
30w | CLI5GM | SUGARHILL3_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 2 | 56 | 57.7 | 103 | No |  | Local Load, continue to monitor and consider future project
30w | STUDY | SUGARHILL3_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 2 | 56 | 57.1 | 102 | No |  | Local Load, continue to monitor and consider future project
35w | BRDGGM | SUGARHILL3_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 2 | 56 | 60.3 | 107.6 | No |  | Local Load, continue to monitor and consider future project
35w | STUDY | SUGARHILL3_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 2 | 56 | 59.5 | 106.3 | No |  | Local Load, continue to monitor and consider future project
30w | CLI5GM | SUGARHILL2_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 3 | 56 | 57.9 | 103.3 | No |  | Local Load, continue to monitor and consider future project
30w | STUDY | SUGARHILL2_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 3 | 56 | 57.3 | 102.3 | No |  | Local Load, continue to monitor and consider future project
35w | BRDGGM | SUGARHILL2_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 3 | 56 | 60.5 | 108 | No |  | Local Load, continue to monitor and consider future project
35w | STUDY | SUGARHILL2_RMCP | 308052 | 1SUGR HL 44.000 | 309348 | SUGAR H2 100.00 | 3 | 56 | 59.7 | 106.6 | No |  | Local Load, continue to monitor and consider future project
30w | MCG1GM | SWEPSONVILL3 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 2 | 44.8 | 48.5 | 108.4 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | SWEPSONVILL3 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 2 | 44.8 | 48.3 | 107.8 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYHAR1VRS | SWEPSONVILL3 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 2 | 44.8 | 50.7 | 113.3 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | SWEPSONVILL3 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 2 | 44.8 | 50.7 | 113.1 | Yes |  | Local Load, continue to monitor and consider future project
30w | MCG1GM | SWEPSONVILL2 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 3 | 44.9 | 48.6 | 108.2 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | SWEPSONVILL2 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 3 | 44.9 | 48.3 | 107.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDYHAR1VRS | SWEPSONVILL2 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 3 | 44.9 | 50.8 | 113.1 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | SWEPSONVILL2 | 308448 | 1SWEPSVL 44.000 | 309369 | SWEPSVI2 100.00 | 3 | 44.9 | 50.7 | 112.9 | Yes |  | Local Load, continue to monitor and consider future project
30s | STUDYRAINVRS | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 58 | 64.8 | 111.7 | No |  | Local Load, continue to monitor and consider future project
30s | STUDY | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 58 | 64.6 | 111.4 | No |  | Local Load, continue to monitor and consider future project
30s | STUDY | TOXAWAY_YB | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 67 | 64.7 | 96.6 | No |  | Local Load, continue to monitor and consider future project
30w | STUDYRAINVRS | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 71 | 68.1 | 95.9 | No |  | Local Load, continue to monitor and consider future project
30w | STUDY | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 71 | 68 | 95.8 | No |  | Local Load, continue to monitor and consider future project
35s | STUDYRAINVRS | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 58 | 67.9 | 117.1 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 58 | 67.9 | 117 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | TOXAWAY_YB | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 67 | 68 | 101.5 | No |  | Local Load, continue to monitor and consider future project
35w | LECCGM | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 71 | 70.8 | 99.8 | No |  | Local Load, continue to monitor and consider future project
35w | STUDY | TOXAWYBK2 | 306066 | TOXAWAY 100.00 | 307167 | 1TOXAWAY 44.000 | 1 | 71 | 70.7 | 99.6 | No |  | Local Load, continue to monitor and consider future project
30w | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 26.5 | 104.9 | No |  | Local Load, continue to monitor and consider future project
30w | DRGSGM | WALNUTCO1 | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 53.8 | 115.7 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | WALNUTCO1 | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 53.7 | 115.5 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | WLNTCSTOKS_B | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 53.7 | 115.5 | Yes |  | Local Load, continue to monitor and consider future project
35w | DRCCGM | WALNUTCO1 | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 55.9 | 120.2 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | WALNUTCO1 | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 55.8 | 120.1 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | WLNTCSTOKS_B | 306809 | WALNUT C 100.00 | 308371 | 1WALNTCV 44.000 | 2 | 46.5 | 55.8 | 120.1 | Yes |  | Local Load, continue to monitor and consider future project
30w | THRPGM | WEBSTERBK1_RMVC | 308488 | 5WEBSTER 161.00 | 308555 | 2WEBSTER 66.000 | 2 | 126 | 129 | 102.4 | Yes |  | Local Load, continue to monitor and consider future project
30w | STUDY | WEBSTERBK1_RMVC | 308488 | 5WEBSTER 161.00 | 308555 | 2WEBSTER 66.000 | 2 | 126 | 128.7 | 102.1 | Yes |  | Local Load, continue to monitor and consider future project
35w | THTKGM | WEBSTERBK1_RMVC | 308488 | 5WEBSTER 161.00 | 308555 | 2WEBSTER 66.000 | 2 | 126 | 135 | 107.1 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | WEBSTERBK1_RMVC | 308488 | 5WEBSTER 161.00 | 308555 | 2WEBSTER 66.000 | 2 | 126 | 134.6 | 106.8 | Yes |  | Local Load, continue to monitor and consider future project
35s | LECCGM | BASE CASE | 307005 | 1ANDRSN+ 44.000 | 307110 | 1STARR 44.000 | 1 | 28.1 | 28 | 97.8 | No |  | Local Load, continue to monitor and consider future project
35s | STUDYLECCGC | BASE CASE | 307005 | 1ANDRSN+ 44.000 | 307110 | 1STARR 44.000 | 1 | 28.1 | 28 | 97.8 | No |  | Local Load, continue to monitor and consider future project
35s | STUDY | BASE CASE | 307005 | 1ANDRSN+ 44.000 | 307110 | 1STARR 44.000 | 1 | 28.1 | 28 | 97.6 | No |  | Local Load, continue to monitor and consider future project
35w | STUDYASH7VRS | LIONMTNBK3 | 307211 | 1LIONMTN 44.000 | 309308 | LIONMTN_2 100.00 | 2 | 41.4 | 39.6 | 95.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | LIONMTNBK3 | 307211 | 1LIONMTN 44.000 | 309308 | LIONMTN_2 100.00 | 2 | 41.4 | 39.5 | 95.5 | Yes |  | Local Load, continue to monitor and consider future project
35w | STUDY | LIONMTNBK2 | 307211 | 1LIONMTN 44.000 | 309308 | LIONMTN_2 100.00 | 3 | 41.4 | 39.6 | 95.6 | Yes |  | Local Load, continue to monitor and consider future project
35w | WYLIGM | LIONMTNBK2 | 307211 | 1LIONMTN 44.000 | 309308 | LIONMTN_2 100.00 | 3 | 41.4 | 39.6 | 95.6 | Yes |  | Local Load, continue to monitor and consider future project
30s | LECCGM | AB_SHADBK2_S | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 83.5 | 98.2 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | STUDY | SHDYGRV_LT2R | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 83.4 | 98.1 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | STUDY | SHADYG2 | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 83.3 | 98 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | STUDY | SHDYGRV_LT2R | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 85.7 | 100.9 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | LESTGM | AB_SHADBK2_S | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 85.6 | 100.8 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | STUDY | SHADYG2 | 307346 | 1SHADY G 44.000 | 309459 | 1SHADY 1 1.0000 | 1 | 85 | 85.6 | 100.7 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | LECCGM | AB_SHADBK1_S | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 83.5 | 99.4 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | STUDY | SHDYGRV_LT1R | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 83.4 | 99.3 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | STUDY | SHADYG1 | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 83.3 | 99.1 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | STUDY | SHDYGRV_LT1R | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 85.7 | 102.1 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | LECCGM | SHADYG1 | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 85.7 | 102 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
35s | STUDY | SHADYG1 | 307346 | 1SHADY G 44.000 | 309460 | 1SHADY 2 1.0000 | 2 | 84 | 85.6 | 101.9 | Yes |  | Moving Normally Open (NO) point on 44 to unload tertiaries at Shady Grove, exclude
30s | STUDYASH7VRS | CHEROKEW-CLI_P21 | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71.8 | 114 | Yes |  | Operating Solution
30s | STUDY | CLFSD5FRVW_W | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71.8 | 114 | Yes |  | Operating Solution
35s | STUDY | CLFSD5_YB | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71.8 | 113.9 | Yes |  | Operating Solution
35s | STUDY | CLFSD5_LT2Y | 306252 | ENOLA RT 100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71.8 | 113.9 | Yes |  | Operating Solution
35s | STUDY | CLFSD5DNCN_W | 306146 | RUTHPV 100.00 | 306285 | OAKLND T 100.00 | 1 | 132 | 141.3 | 102.6 | Yes |  | Operating Solution
30s | LECCGM | KNOLLWOODB | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 134.9 | 113.7 | Yes |  | Operating Solution
30s | STUDY | KNOLLWOODB | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 134.9 | 113.3 | Yes |  | Operating Solution
30s | STUDY | WSPTGPWOOD_B_RMVCAP | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 134.9 | 113.2 | Yes |  | Operating Solution
35s | LECCGM | KNOLLWOODB | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 141.1 | 118.8 | Yes |  | Operating Solution
35s | STUDY | KNOLLWOODB | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 141.1 | 118.5 | Yes |  | Operating Solution
35s | STUDY | WSPTGPWOOD_B_TGLCAP | 306262 | KNOLWD W 100.00 | 306305 | W SPTBRG 100.00 | 1 | 120 | 141.1 | 118.5 | Yes |  | Operating Solution
30s | STUDY | WFRKLEMLEY_B | 306566 | CHINA GR 100.00 | 309958 | LANDIS4 100.00 | 1 | 120 | 117.1 | 96.3 | Yes |  | Operating Solution
35s | STUDY | WFRKLEMLEY_B | 306566 | CHINA GR 100.00 | 309958 | LANDIS4 100.00 | 1 | 120 | 117.9 | 96.8 | Yes |  | Operating Solution
35s | STUDY | HORSHORUGB_B | 306190 | PISGAH 100.00 | 308711 | BLANTYRERET 100.00 | 2 | 132 | 126.2 | 96 | Yes |  | Operating Solution
30s | LECCGM | TAYLORSB | 306198 | TIGER 100.00 | 306212 | DUK 306212 100.00 | 1 | 132 | 138.6 | 102.5 | Yes |  | Operating Solution
35s | LECCGM | TAYLORSB | 306198 | TIGER 100.00 | 306212 | DUK 306212 100.00 | 1 | 132 | 133.5 | 98.6 | Yes |  | Operating Solution
30w | STUDY | TGRTAYLORS_W | 306305 | W SPTBRG 100.00 | 306307 | WALDEN T 100.00 | 1 | 114 | 108.8 | 95.6 | Yes |  | Operating Solution
35s | STUDY | TGRTAYLORS_W | 306305 | W SPTBRG 100.00 | 306307 | WALDEN T 100.00 | 1 | 91 | 87.8 | 96.9 | Yes |  | Operating Solution
35s | CAT1GM | NEWPORT_UGBL_TC | 306416 | WATEREE 100.00 | 309837 | RANGERLN 100.00 | 2 | 116 | 123.4 | 104.2 | Yes |  | Operating Solution
30s | STUDYRAINVRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 152 | 174.9 | 117.7 | Yes |  | Operating Solution
30w | STUDYASH5VRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 181 | 180.2 | 97.5 | Yes |  | Operating Solution
35s | STUDYSCPSVRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 152 | 183.2 | 123.7 | Yes |  | Operating Solution
35w | STUDYRICHVRS | WESTMINW-CE_P21 | 306062 | SENCA TB 100.00 | 306078 | DUK 306078 100.00 | 1 | 181 | 186.4 | 100.8 | Yes |  | Operating Solution
30s | STUDYRAINVRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 152 | 145.8 | 100.4 | Yes |  | Operating Solution
35s | STUDYVCS1VRS | WESTMINW-CE_P21 | 306071 | WESTMNS+ 100.00 | 309747 | BREC35 100.00 | 1 | 152 | 152.5 | 105.7 | Yes |  | Operating Solution
30s | STUDYRAINVRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 152 | 167.9 | 115.2 | Yes |  | Operating Solution
30w | STUDYASH5VRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 181 | 176.5 | 96.1 | Yes |  | Operating Solution
35s | STUDYRICHVRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 152 | 175.6 | 121.2 | Yes |  | Operating Solution
35w | STUDYRICHVRS | WESTMINW-CE_P21 | 306078 | DUK 306078 100.00 | 309747 | BREC35 100.00 | 1 | 181 | 182.4 | 99.4 | Yes |  | Operating Solution
30s | STUDYRAINVRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 152 | 152.5 | 100.6 | Yes |  | Operating Solution
30w | STUDYRICHVRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 181 | 191.7 | 104.1 | Yes |  | Operating Solution
35s | STUDYRICHVRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 152 | 158.1 | 104.4 | Yes |  | Operating Solution
35w | STUDYRICHVRS | WESTMINB-CE_P21 | 306071 | WESTMNS+ 100.00 | 306081 | BLREC26 100.00 | 1 | 181 | 197.7 | 107.4 | Yes |  | Operating Solution
35s | ABPVGM | WHETSTONB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 117 | 152.9 | 134.9 | Yes |  | Operating Solution
35w | STUDY | HILLTOP_RB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 173 | 118 | Yes |  | Operating Solution
35w | MCG1GM | WHETSTONB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 171.8 | 115.1 | Yes |  | Operating Solution
35w | STUDY | WHETSTONB | 306377 | HILLTOP 100.00 | 309377 | DUK 309377 100.00 | 2 | 154 | 171.7 | 114.7 | Yes |  | Operating Solution
30w | STUDY | HLTPWHETSTONE_B | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 3 | 45.7 | 47.9 | 104.9 | No |  | Operating Solution
35w | STUDY | HILLTOP_RB | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 3 | 45.7 | 49.1 | 107.5 | No |  | Operating Solution
35w | STUDY | HLTPWHETSTONE_B | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 3 | 45.7 | 47.9 | 104.8 | No |  | Operating Solution
30w | STUDY | HLTPWHETSTONE_B | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 4 | 24.2 | 27.5 | 113.5 | Yes |  | Operating Solution
35w | STUDY | HILLTOP_RB | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 4 | 24.2 | 28.1 | 116.3 | Yes |  | Operating Solution
35w | STUDY | HLTPWHETSTONE_B | 307709 | 1HILLTOP 44.000 | 309373 | HILLTOP34 100.00 | 4 | 24.2 | 27.5 | 113.5 | Yes |  | Operating Solution
30s | STUDY | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 43.5 | 101.3 | Yes |  | Operating Solution
30s | WYLIGM | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 43.5 | 101.3 | Yes |  | Operating Solution
30w | OXFDGM | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 69.8 | 162.6 | Yes |  | Operating Solution
30w | STUDY | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 68.6 | 160 | Yes |  | Operating Solution
35s | STUDY | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 45.6 | 106.4 | Yes |  | Operating Solution
35s | WYLIGM | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 45.6 | 106.4 | Yes |  | Operating Solution
35w | OXFDGM | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 75.4 | 175.7 | Yes |  | Operating Solution
35w | STUDY | TAYLORSV2 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 1 | 42.9 | 72.7 | 169.5 | Yes |  | Operating Solution
30s | STUDY | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 43.5 | 101.4 | Yes |  | Operating Solution
30s | WYLIGM | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 43.5 | 101.4 | Yes |  | Operating Solution
30w | OXFDGM | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 69.8 | 162.8 | Yes |  | Operating Solution
30w | STUDY | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 68.7 | 160.1 | Yes |  | Operating Solution
35s | STUDY | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 45.6 | 106.4 | Yes |  | Operating Solution
35s | WYLIGM | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 45.6 | 106.4 | Yes |  | Operating Solution
35w | OXFDGM | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 75.5 | 176 | Yes |  | Operating Solution
35w | STUDY | TAYLORSV1 | 308066 | 1TYLRSVL 44.000 | 309350 | TYLRSVI2 100.00 | 2 | 42.9 | 72.8 | 169.7 | Yes |  | Operating Solution
30w | WYLIGM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 26.5 | 104.9 | No |  | Operating Solution
35s | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 24.6 | 97.2 | No |  | Operating Solution
35s | WYLIGM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 24.6 | 97.2 | No |  | Operating Solution
35w | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 27.3 | 108 | No |  | Operating Solution
35w | WYLIGM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 2 | 25.3 | 27.3 | 108 | No |  | Operating Solution
30w | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 26.4 | 104.2 | No |  | Operating Solution
30w | WYLIGM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 26.4 | 104.2 | No |  | Operating Solution
35s | CLI6GM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 24.4 | 96.6 | No |  | Operating Solution
35s | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 24.4 | 96.5 | No |  | Operating Solution
35w | CLI6GM | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 27.1 | 107.3 | No |  | Operating Solution
35w | STUDY | WALHABK4 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 3 | 25.3 | 27.1 | 107.2 | No |  | Operating Solution
30s | STUDY | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 24 | 96.7 | Yes |  | Operating Solution
30s | WYLIGM | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 24 | 96.7 | Yes |  | Operating Solution
30w | WYLIGM | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 26.8 | 108 | Yes |  | Operating Solution
30w | STUDY | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 26.8 | 107.9 | Yes |  | Operating Solution
35s | CLI6GM | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 24.8 | 100.1 | Yes |  | Operating Solution
35s | STUDY | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 24.8 | 100 | Yes |  | Operating Solution
35w | STUDY | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 27.6 | 111.1 | Yes |  | Operating Solution
35w | WYLIGM | WALHABK2 | 307177 | 1WALHALA 44.000 | 309306 | WALHALL2 100.00 | 4 | 24.8 | 27.6 | 111.1 | Yes |  | Operating Solution
30s | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 422 | 462.5 | 110 | Yes |  | Operating Solution
35s | LECCGM | LONDONCREEKW | 306265 | 6RIVERVW 230.00 | 309165 | 6LDNCKB_RTR 230.00 | 1 | 422 | 414 | 98.2 | Yes |  | Operating Solution
30s | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 422 | 462.5 | 110 | Yes |  | Operating Solution
35s | LECCGM | LONDONCREEKW | 306236 | 6PEACH V 230.00 | 309165 | 6LDNCKB_RTR 230.00 | Z1 | 422 | 414 | 98.2 | Yes |  | Operating Solution
30s | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 422 | 462.5 | 110 | Yes |  | Operating Solution
35s | LECCGM | LONDONCREEKB | 306265 | 6RIVERVW 230.00 | 309166 | 6LDNCKW_RTR 230.00 | 2 | 422 | 414 | 98.2 | Yes |  | Operating Solution
30s | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 422 | 462.5 | 110 | Yes |  | Operating Solution
35s | LECCGM | LONDONCREEKB | 306236 | 6PEACH V 230.00 | 309166 | 6LDNCKW_RTR 230.00 | Z2 | 422 | 414 | 98.2 | Yes |  | Operating Solution
30s | STUDY | CENT230HT1 | 306004 | 6CENTRAL 230.00 | 309406 | 1CENTRL 2 1.0000 | 2 | 277 | 275.3 | 99.4 | Yes |  | Operating Solution
35s | STUDY | CENT230HT1 | 306004 | 6CENTRAL 230.00 | 309406 | 1CENTRL 2 1.0000 | 2 | 277 | 285.5 | 103.1 | Yes |  | Operating Solution
30s | STUDY | CENT230HT1 | 309406 | 1CENTRL 2 1.0000 | 309502 | CENT2 100.00 | 2 | 268 | 268.9 | 100.4 | No |  | Operating Solution
35s | STUDY | CENT230HT1 | 309406 | 1CENTRL 2 1.0000 | 309502 | CENT2 100.00 | 2 | 268 | 278 | 103.7 | No |  | Operating Solution
30s | STUDY | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 42 | 105.1 | Yes |  | Operating Solution
30s | STUDY | ENO_LT1R | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 42.1 | 105.1 | Yes |  | Operating Solution
30s | WYLIGM | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 42 | 105.1 | Yes |  | Operating Solution
30s | STUDY | ENO_LT1R | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 42.1 | 105.1 | Yes |  | Operating Solution
30w | STUDY | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 51.6 | 129.1 | Yes |  | Operating Solution
30w | STUDY | ENO230HT1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 51.6 | 129.1 | Yes |  | Operating Solution
30w | WYLIGM | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 51.6 | 129.1 | Yes |  | Operating Solution
30w | STUDY | ENO230HT1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 51.6 | 129.1 | Yes |  | Operating Solution
35s | STUDY | ENO_LT1R | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 44 | 110.1 | Yes |  | Operating Solution
35s | STUDY | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 44 | 110 | Yes |  | Operating Solution
35s | WYLIGM | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 44 | 110 | Yes |  | Operating Solution
35w | STUDY | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 53.6 | 133.9 | Yes |  | Operating Solution
35w | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 53.5 | 133.9 | Yes |  | Operating Solution
35w | WYLIGM | ENO1 | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 53.6 | 133.9 | Yes |  | Operating Solution
35w | STUDY | ENO_LT1Y | 308422 | 1ENO 44.000 | 309413 | 1ENO 3 1.0000 | 3 | 40 | 53.5 | 133.9 | Yes |  | Operating Solution
30w | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 83.8 | 99.8 | Yes |  | Operating Solution
35w | RDHSGM | LONGVIEW3 | 307989 | 1LONVIEW 44.000 | 309423 | 1LONGV 2 1.0000 | 2 | 84 | 86.7 | 103.2 | Yes |  | Operating Solution
30w | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 83.2 | 109.4 | Yes |  | Operating Solution
35w | RDHSGM | LONGVIEW2 | 307989 | 1LONVIEW 44.000 | 309424 | 1LONGV 3 1.0000 | 3 | 76 | 86.1 | 113.3 | Yes |  | Operating Solution
30w | STUDY | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 84 | 98.8 | Yes |  | Operating Solution
30w | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 84 | 98.8 | Yes |  | Operating Solution
35w | STUDY | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 86.8 | 102.1 | Yes |  | Operating Solution
35w | WYLIGM | MITCHR1 | 308325 | 1MITCH R 44.000 | 309430 | 1MITCH 3 1.0000 | 3 | 85 | 86.8 | 102.1 | Yes |  | Operating Solution
35w | CLI5GM | PEACHV3C | 307542 | 1PEACH V 44.000 | 309445 | 1PEACH 1 1.0000 | 1 | 44.8 | 42.8 | 95.5 | Yes |  | Operating Solution
35w | STUDY | PEACHV3C | 307542 | 1PEACH V 44.000 | 309445 | 1PEACH 1 1.0000 | 1 | 44.8 | 42.8 | 95.4 | Yes |  | Operating Solution
30s | DRCCGM | SADLER3 | 306058 | 6SADLERY 230.00 | 309458 | 1SADLE 4 1.0000 | 4 | 534 | 554.1 | 103.8 | Yes |  | Operating Solution
35s | DRCCGM | SADLER3 | 306058 | 6SADLERY 230.00 | 309458 | 1SADLE 4 1.0000 | 4 | 534 | 567.5 | 106.3 | Yes |  | Operating Solution
30s | DRCCGM | SADLER3 | 309458 | 1SADLE 4 1.0000 | 309518 | SADL4 100.00 | 4 | 534 | 554.1 | 103.8 | Yes |  | Operating Solution
35s | DRCCGM | SADLER3 | 309458 | 1SADLE 4 1.0000 | 309518 | SADL4 100.00 | 4 | 534 | 567.5 | 106.3 | Yes |  | Operating Solution
30w | WATRGM | SHELBY4 | 307790 | 1SHELBY 44.000 | 309461 | 1SHELB 2 1.0000 | 2 | 67 | 65.3 | 97.5 | Yes |  | Operating Solution
30w | STUDY | SHELBY4 | 307790 | 1SHELBY 44.000 | 309461 | 1SHELB 2 1.0000 | 2 | 67 | 65.2 | 97.3 | Yes |  | Operating Solution
35w | STUDY | SHLB230HT4 | 307790 | 1SHELBY 44.000 | 309462 | 1SHELB 3 1.0000 | 3 | 67 | 67.4 | 100.6 | Yes |  | Operating Solution
35w | STUDYSCPSVRS | SHELBY4C | 307790 | 1SHELBY 44.000 | 309462 | 1SHELB 3 1.0000 | 3 | 67 | 67.4 | 100.5 | Yes |  | Operating Solution
35w | STUDY | SHELBY4C | 307790 | 1SHELBY 44.000 | 309462 | 1SHELB 3 1.0000 | 3 | 67 | 67.3 | 100.4 | Yes |  | Operating Solution
30s | WGPVGM | SHELBY2 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 53.6 | 95.7 | Yes |  | Operating Solution
30w | STUDY | SHELBY2 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 65.7 | 117.4 | Yes |  | Operating Solution
30w | WYLIGM | SHELBY2 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 65.8 | 117.4 | Yes |  | Operating Solution
35s | WGPVGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 56 | 100.1 | Yes |  | Operating Solution
35w | STUDY | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 68 | 121.5 | Yes |  | Operating Solution
35w | WYLIGM | SHELBY3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 56 | 68 | 121.5 | Yes |  | Operating Solution
35w | STUDY | SHLB230HT3 | 307790 | 1SHELBY 44.000 | 309463 | 1SHELB 4 1.0000 | 4 | 70 | 68.1 | 97.2 | Yes |  | Operating Solution
35s | RDHSGM | RHODHISS5 | 307989 | 1LONVIEW 44.000 | 308029 | 1RHODHSR 44.000 | 1 | 37.7 | 36.5 | 95.6 | No |  | Re-dispatch generation at Rhod hiss
35w | STUDY | RHODHISSBUS | 307989 | 1LONVIEW 44.000 | 308029 | 1RHODHSR 44.000 | 1 | 51 | 53.2 | 99.7 | Yes |  | Re-dispatch generation at Rhodhiss
35w | RDHSGM | RHODHISS5 | 307989 | 1LONVIEW 44.000 | 308029 | 1RHODHSR 44.000 | 1 | 49.2 | 48.4 | 98.1 | Yes |  | Re-dispatch generation at Rhodhiss
35w | STUDY | CLOVER_BUSR1_RMVCAP | 307721 | 1KING CK 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 41.8 | 38.5 | 96.8 | Yes | Yes
35w | STUDY | CLOVER_BUSR1_RMVCAP | 307748 | 1NINE 9 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 54 | 56.5 | 104.7 | Yes | Yes
35s | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 60 | 79.3 | 132.2 | Yes | Yes
35w | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 60 | 73.9 | 123.1 | Yes | Yes
35s | STUDY | WDLN230CB13A | 307839 | 1WYLIE 44.000 | 308188 | 1PNVL T2 44.000 | 1 | 52 | 51.7 | 96.8 | No | Yes
35s | STUDY | CLOVER_BUSR1_RMVCAP | 307655 | 1CARVER 44.000 | 307844 | 1YORKEC1 44.000 | 1 | 32 | 26.2 | 131.5 | Yes | Yes
35s | STUDY | CLOVER_BUSR1_RMVCAP | 307721 | 1KING CK 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 33.4 | 53.4 | 196.3 | Yes | Yes
35s | STUDY | CLOVER_BUSR1_RMVCAP | 307721 | 1KING CK 44.000 | 307843 | 1YORKE14 44.000 | 1 | 33.4 | 46.4 | 194.4 | Yes | Yes
35s | STUDY | CLOVER_BUSR1_RMVCAP | 307748 | 1NINE 9 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 45.6 | 71.8 | 172.6 | Yes | Yes
35s | STUDY | CLOVER_BUSR1_RMVCAP | 307843 | 1YORKE14 44.000 | 307844 | 1YORKEC1 44.000 | 1 | 59 | 37.4 | 96.9 | No | Yes
30s | STUDY | CLOVER_BUSR1_RMVCAP | 307655 | 1CARVER 44.000 | 307844 | 1YORKEC1 44.000 | 1 | 32 | 25.6 | 117.2 | Yes | Yes
30s | STUDY | CLOVER_BUSR1_RMVCAP | 307721 | 1KING CK 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 33.4 | 50.2 | 176.6 | Yes | Yes
30s | STUDY | CLOVER_BUSR1_RMVCAP | 307721 | 1KING CK 44.000 | 307843 | 1YORKE14 44.000 | 1 | 33.4 | 44.4 | 174.4 | Yes | Yes
30s | STUDY | CLOVER_BUSR1_RMVCAP | 307748 | 1NINE 9 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 45.6 | 66.9 | 156.7 | Yes | Yes
30w | STUDY | CLOVER_BUSR1_RMVCAP | 307748 | 1NINE 9 44.000 | 307798 | 1SHRN GT 44.000 | 1 | 54 | 53.6 | 98.8 | Yes | Yes
30s | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 60 | 76.7 | 127.8 | Yes | Yes
30w | STUDY | TIGER_LT3R | 307350 | 1TIGER 44.000 | 309467 | 1TIGER 5 1.0000 | 5 | 60 | 70.5 | 117.5 | Yes | Yes
30w | DRCCGM | MADISON3_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 2 | 69 | 70.3 | 101.8 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
30w | STUDY | MADISON3_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 2 | 69 | 70 | 101.4 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
35w | DRCCGM | MADISON3_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 2 | 69 | 68.2 | 98.8 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
35w | STUDY | MADISON3_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 2 | 69 | 67.7 | 98.1 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
30w | DRCCGM | MADISON2_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 3 | 69 | 70.3 | 101.9 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
30w | STUDY | MADISON2_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 3 | 69 | 70 | 101.5 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
35w | DRCCGM | MADISON2_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 3 | 69 | 68.2 | 98.9 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
35w | STUDY | MADISON2_RMVCAP | 308312 | 1MADISON 44.000 | 309361 | MADISON2 100.00 | 3 | 69 | 67.7 | 98.1 | Yes |  | W210482 (New Project) - Add third transformer at Madison Tie
35s | STUDY | LAURENRAB_W_CS#_RMVCAP | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 42.6 | 102.7 | No | Yes
35w | STUDY | LAURENS_YB_CS#_TGLCAP | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 40.4 | 98.5 | No | Yes
35w | STUDY | LAURENRAB_W_CS#_TGLCAP | 307942 | CLINTON 100.00 | 308794 | CLINTON TB 100.00 | Z1 | 41.6 | 40.4 | 98.5 | No | Yes
35s | STUDY | LAURENRAB_W_CS#_RMVCAP | 307432 | 1CLINTON 44.000 | 307942 | CLINTON 100.00 | 1 | 23.7 | 24.8 | 104.5 | Yes | Yes
35w | STUDY | LAURENS_YB_CS#_TGLCAP | 307432 | 1CLINTON 44.000 | 307942 | CLINTON 100.00 | 1 | 23.7 | 23.4 | 98.9 | Yes | Yes
35w | STUDY | LAURENRAB_W_CS#_TGLCAP | 307432 | 1CLINTON 44.000 | 307942 | CLINTON 100.00 | 1 | 23.7 | 23.4 | 98.9 | Yes | Yes
35s | CAT1GM | OAKVALEW | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 1 | 270 | 279.3 | 99.7 | No |  | W220506 (New Project) - Replace switches to get full line rating
35s | STUDY | OAKVALEW | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 1 | 270 | 273.5 | 97.5 | No |  | W220506 (New Project) - Replace switches to get full line rating
35s | STUDY | SHDYGPDMNT_W | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 1 | 270 | 269.6 | 97.3 | No |  | W220506 (New Project) - Replace switches to get full line rating
35s | STUDY | SHADYLEE_RB | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 2 | 270 | 283.3 | 101.9 | No |  | W220506 (New Project) - Replace switches to get full line rating
35s | CAT1GM | OAKVALEB | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 2 | 270 | 279.3 | 99.7 | No |  | W220506 (New Project) - Replace switches to get full line rating
35s | STUDY | OAKVALEB | 306183 | OAKVALE 100.00 | 306195 | SHADY GR 100.00 | 2 | 270 | 273.5 | 97.5 | No |  | W220506 (New Project) - Replace switches to get full line rating
30s | STUDY | CLFSD5_YB | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 65 | 69.7 | 114.2 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLFSD5FRVW_W | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 65 | 69.7 | 114.2 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDYRICHVRS | CHEROKEW-CLI_P21 | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 65 | 69.7 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDY | CLIFSID5LN_W | 307276 | DUK 307276 100.00 | 309376 | STR 173 100.00 | 1 | 65 | 69.7 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLFSD5_YB | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 65 | 70.6 | 114.1 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLFSD5FRVW_W | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 65 | 70.6 | 114.1 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDYRICHVRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 65 | 70.6 | 113.9 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDY | CLIFSID5LN_W | 308792 | CHESNEE T WH100.00 | 308803 | SPARTAN T WH100.00 | 1 | 65 | 70.6 | 113.9 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDYVCS1VRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLIFSID5LN_W | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDYRICHVRS | CHEROKEW-CLI_P21 | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71 | 113.9 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDY | CLIFSID5LN_W | 308792 | CHESNEE T WH100.00 | 309168 | MAYO T 100.00 | 1 | 65 | 71 | 113.9 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLFSD5_YB | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 65 | 70.1 | 114.2 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CLFSD5FRVW_W | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 65 | 70.1 | 114.2 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDYRICHVRS | CHEROKEW-CLI_P21 | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 65 | 70.1 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
35s | STUDY | CLIFSID5LN_W | 308803 | SPARTAN T WH100.00 | 309376 | STR 173 100.00 | 1 | 65 | 70.1 | 114 | Yes |  | W250214 (New Project) - Rebuild Cherokee lines between Chesnee and AZP
30s | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 1 | 25.6 | 25.9 | 101.2 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
30w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 1 | 25.6 | 32.7 | 127.7 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
35s | STUDY | CAMPOBELL_RB | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 1 | 25.6 | 27 | 105.4 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
35s | STUDY | CAMPCLFSDBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 1 | 25.6 | 27 | 105.4 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
35w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 1 | 25.6 | 34.3 | 134 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
30w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 2 | 29.9 | 33.3 | 111.5 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
35w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 2 | 29.9 | 35 | 117 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
30w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 3 | 29.1 | 33.3 | 114.4 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
35w | STUDY | CAMPHARLYBL | 307479 | 1INMAN 44.000 | 309323 | INMAN 2 100.00 | 3 | 29.1 | 34.9 | 120.1 | Yes |  | W250285 (New Project) - Add breakers to high side of transformers
30s | STUDYHAR1VRS | PARKWOOD_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 153.7 | 101.8 | Yes | Yes
30s | STUDYHAR1VRS | DELTAB-PARK_P21 | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 147.5 | 98 | Yes | Yes
30s | STUDY | PARKWOOD_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 147.9 | 97.4 | Yes | Yes
30s | STUDY | PLGR500OCB4_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 147.9 | 97.4 | Yes | Yes
35s | STUDYHAR1VRS | PARKWOOD_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 160.2 | 107.4 | Yes | Yes
35s | STUDY | PARKWOOD_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 154.6 | 102.8 | Yes | Yes
35s | STUDY | PLGR500OCB4_EHV | 306852 | ASHE ST 100.00 | 306875 | DURHAM 100.00 | 1 | 152 | 154.6 | 102.8 | Yes | Yes
35s | STUDY | RURLHPINCL_W | 306727 | MNTROYRT 100.00 | 306788 | RURAL HL 100.00 | 1 | 213 | 212.3 | 96.9 | Yes | Yes
35s | AMPVGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 183 | 186.1 | 99.1 | Yes | Yes
35w | LOOKGM | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 183 | 208.1 | 111.1 | No | Yes
35w | STUDY | STAMYMKSVL_W | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 183 | 197.4 | 105.4 | No | Yes
35w | STUDY | BEULAHW | 306454 | ENRG U18 100.00 | 306472 | LOOKOUT 100.00 | 1 | 183 | 192.9 | 103 | No | Yes
30w | STUDY | STAMEYOXFORD | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 185.2 | 99.8 | Yes | Yes
35s | STUDYURQHVRS | BEULAHBL-STA_P21 | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 218.6 | 116.1 | Yes | Yes
35s | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 215.9 | 115.6 | Yes | Yes
35s | AMPVGM | BEULAHB | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 186.1 | 99.1 | Yes | Yes
35w | STUDY | STAMYMKSVL_B | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 245.9 | 132 | Yes | Yes
35w | LOOKGM | BEULAHB | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 208.1 | 111.1 | Yes | Yes
35w | STUDY | BEULAHB | 306472 | LOOKOUT 100.00 | 309286 | ENGR U18 W 100.00 | 1 | 183 | 192.9 | 103 | Yes | Yes
30s | STUDY | STONEW_RB_RMVCAP | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 132 | 164.1 | 130.2 | Yes | Yes
30s | STUDY | STNWTRIVER_B_RMVCAP | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 132 | 164.1 | 130.2 | Yes | Yes
35s | STUDY | STONEW_RB_RMVCAP | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 132 | 171.8 | 136.9 | Yes | Yes
35s | STUDY | STNWTRIVER_B_RMVCAP | 306681 | WESTFORK 100.00 | 306685 | WILDCAT 100.00 | 1 | 132 | 171.8 | 136.9 | Yes | Yes
30s | STUDY | HARSBRG_LT4R_CS | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 135 | 202.5 | 150.9 | No | Yes
30w | STUDY | HBURGNCHLT_B_CS | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 159 | 160.3 | 99.3 | Yes | Yes
35s | STUDYRICHVRS | CONCRDBS-HB_P21 | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 135 | 132.6 | 97.5 | No | Yes
35s | STUDY | HARSBRG_LT4R_FS | 306573 | CONCORD 100.00 | 309611 | CONCORD4 100.00 | 1 | 135 | 132.6 | 97.4 | No | Yes
30s | STUDY | HARSBRG_LT4R_CS | 306638 | DUK 306638 100.00 | 306703 | CONCORD3 100.00 | 1 | 152 | 161.5 | 109.9 | Yes | Yes
30s | STUDY | HBURGCRABO_W | 306600 | HARRISBG 100.00 | 308863 | HIC GRO BL 100.00 | 1 | 132 | 136.4 | 102.7 | Yes | Yes
35s | STUDY | HBURGCRABO_W | 306600 | HARRISBG 100.00 | 308863 | HIC GRO BL 100.00 | 1 | 132 | 136.3 | 102.7 | Yes | Yes
30s | STUDY | HBURGCRABO_B_CS | 306600 | HARRISBG 100.00 | 306601 | HCKRY GR 100.00 | 1 | 132 | 141.7 | 106.8 | Yes | Yes
35s | STUDY | HBURGCRABO_B_FS | 306600 | HARRISBG 100.00 | 306601 | HCKRY GR 100.00 | 1 | 132 | 138.1 | 104 | Yes | Yes
30s | STUDY | ENO_YB | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 2 | 197 | 192.8 | 95.1 | Yes | Yes
35s | STUDY | ENO_YB | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 2 | 197 | 203.3 | 101.1 | Yes | Yes
35s | STUDY | ENOBRAGTWN_B | 306868 | CREST ST 100.00 | 306881 | ENO 100.00 | 2 | 197 | 192.3 | 96.6 | Yes | Yes
35s | STUDY | CLIFFSDE2P23MB | 306389 | DUK 306389 100.00 | 306401 | SHELBY 100.00 | 1 | 105 | 105.9 | 99.1 | Yes | Yes
35w | STUDY | CLIFFSDE2P23MB | 306389 | DUK 306389 100.00 | 306401 | SHELBY 100.00 | 1 | 132 | 129 | 97.1 | Yes | Yes
35s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 308923 | WENTW BL 100.00 | 1 | 105 | 104.2 | 96.2 | Yes | Yes
30s | BUCCGM | DEEPRVRW | 306902 | GREENSBR 100.00 | 308930 | FRIEND B 100.00 | 1 | 132 | 126.3 | 96.6 | Yes | Yes
35s | BUCCGM | DEEPRVRW | 306902 | GREENSBR 100.00 | 308930 | FRIEND B 100.00 | 1 | 132 | 129.4 | 99.6 | Yes | Yes
35s | STUDY | DEEPRVRW | 306902 | GREENSBR 100.00 | 308930 | FRIEND B 100.00 | 1 | 132 | 126 | 96.9 | Yes | Yes
30s | STUDY | ASHSTDELTA_W | 306880 | ELLIS RD_B 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 129 | 122.7 | 97.4 | Yes | Yes
35s | STUDY | ASHSTDELTA_W | 306880 | ELLIS RD_B 100.00 | 306952 | R TRNGLE_B 100.00 | 1 | 129 | 126.4 | 101.2 | Yes | Yes
30s | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 137.8 | 108.2 | Yes | Yes
30s | STUDY | PARKWDRAM_B | 308929 | ELLIS RD_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 130.8 | 102.6 | Yes | Yes
35s | STUDY | PARKWOOD_RB | 308929 | ELLIS RD_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 144.3 | 114.3 | Yes | Yes
35s | STUDY | PARKWDRAM_B | 308929 | ELLIS RD_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 136.9 | 108.4 | Yes | Yes
30s | STUDY | PARKWOOD_RB | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 152.9 | 119.7 | Yes | Yes
30s | STUDY | PARKWDRAM_B | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 145.9 | 114.1 | Yes | Yes
30w | STUDY | PARKWOOD_RB | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 162 | 154.4 | 95.1 | Yes | Yes
35s | STUDY | PARKWOOD_RB | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 159.5 | 125.9 | Yes | Yes
35s | STUDY | PARKWDRAM_B | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 129 | 152.1 | 120 | Yes | Yes
35w | STUDY | PARKWOOD_RB | 308940 | R TRNGLE_W 100.00 | 309753 | DUK 309753 100.00 | 1 | 162 | 154.4 | 95.1 | Yes | Yes
30s | CAT1GM | WOODLA5 | 306611 | LAKEWOOD 100.00 | 306649 | REMOUNT 100.00 | 1 | 166 | 158.9 | 95.2 | Yes | Yes
35s | CAT1GM | WOODLA5 | 306611 | LAKEWOOD 100.00 | 306649 | REMOUNT 100.00 | 1 | 166 | 162.9 | 97.3 | Yes | Yes
30s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 2 | 105 | 125.5 | 114.8 | Yes | Yes
35s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 2 | 105 | 127.7 | 117.9 | Yes | Yes
30s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 1 | 105 | 128 | 117 | Yes | Yes
35s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 1 | 105 | 130.3 | 120.2 | Yes | Yes
30s | STUDY | WFRKCABRUS_W | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 1 | 132 | 163.5 | 125.8 | Yes | Yes
35s | STUDY | WFORKODELL_W | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 1 | 132 | 167.6 | 131.8 | Yes | Yes
30s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 2 | 132 | 163.6 | 126 | Yes | Yes
35s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 2 | 132 | 171.4 | 132.4 | Yes | Yes
30s | STUDY | LEEC_YB_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 519 | 802.3 | 148.4 | No | Yes
30s | STUDY | LEESREDYRV_W#_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 519 | 751.2 | 139 | No | Yes
30w | STUDY | LEEC_YB_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 519 | 817.4 | 150.9 | Yes | Yes
30w | STUDY | LEESREDYRV_W#_NOGEN | 306041 | LEE 100.00 | 308622 | LEE CC 100.00 | 1 | 519 | 758.5 | 140 | Yes | Yes
35s | SHPVGM | SWPSNVLBL | 306938 | MEBANE 100.00 | 306968 | TROLNGWD 100.00 | 1 | 132 | 127.8 | 95.7 | Yes | Yes
35s | STUDYROB2VRS | SWPSNVLBL_P21 | 306938 | MEBANE 100.00 | 306968 | TROLNGWD 100.00 | 1 | 132 | 127 | 95.1 | Yes | Yes
30s | STUDY | WFRKCABRUS_W | 306681 | WESTFORK 100.00 | 308892 | LANGTREE TAP100.00 | 4 | 165 | 164 | 103 | Yes | Yes
35s | STUDY | WFORKODELL_W | 306681 | WESTFORK 100.00 | 308892 | LANGTREE TAP100.00 | 4 | 165 | 171.5 | 107.9 | Yes | Yes
30s | STUDY | WFRKLEMLEY_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 3 | 165 | 163.8 | 102.9 | Yes | Yes
35s | STUDY | WFRKCABRUS_B | 306629 | MORESVIL 100.00 | 306681 | WESTFORK 100.00 | 3 | 165 | 171.4 | 108.1 | Yes | Yes
30s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 4 | 105 | 125.2 | 114.5 | Yes | Yes
35s | STUDY | DANRIVSLN_W | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 4 | 105 | 127.4 | 117.6 | Yes | Yes
30s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 3 | 105 | 127.7 | 116.7 | Yes | Yes
35s | STUDY | DANRIVS_YB_WINDMERE | 306737 | DAN RIV 100.00 | 306790 | SADLER 100.00 | 3 | 105 | 130 | 120 | Yes | Yes
35s | MCG1GM | DEPP106 | 306333 | 6NEWPORT 230.00 | 306541 | 6MORN ST 230.00 | 1 | 421 | 425.8 | 101.1 | Yes | Yes
35s | STUDY | DEPP106 | 306333 | 6NEWPORT 230.00 | 306541 | 6MORN ST 230.00 | 1 | 421 | 404.1 | 95.7 | Yes | Yes
30s | STUDY | MORN230CB25# | 306541 | 6MORN ST 230.00 | 309552 | MORN4 100.00 | 4 | 197 | 199.2 | 101.1 | Yes | Yes

## Projects to Add to Plan
| Project Number | Project Description | Project Cost ($ M) | In Service Date
Addresses Local Reliability Needs | CTPCDEC03 | Correct Clearance Issues on the Clear Creek Lines to increase the line's raiting | 2 | Conceptual
| CTPCDEC04 | Replace Anciliary Equipment on the Glen Springs line to increase the Line's Ratings | 2 | Conceptual
| CTPCDEC05 | Add capacitor banks at Lake Emory | 10 | Conceptual
| W210482 | Install additional 100/44 kV transformer at Madison Tie | 2.4 | 2034-06-20
| W220506 | Upgrade Switches at Oakvale Tie | 0.86 | 2027-11-30
| W250214 | Rebuild the Cherokee LInes between AZP Tap and Chesnee Tie with 1158 ACSS/TW | 6.4 | 2028-10-23
| W250285 | Add breakers at Campobello Tie | 0.74 | 2032-09-02
| W250072 | Taylors 100kV Line - Rebuild between Tiger Tie and Customer Station with 795 ACSS/TW | 1.79 | 2033-05-13
| W250312 | Shelby Tie - Replace Bank 4 | 7.91 | 2033-03-25
| W250281 | Lemley 100 kV Bl & Wh Lines 3 span clearance fix and AEU contains D-Line Work | 6.94 | 2033-04-29
| W250207 | Cliffside 100 kV Lines - Rebuild lines between Cliffside 5 and Customer Tap with 1158 ACSS/TW | 28.78 | 2030-02-28
| W250212 | Duncan 100 kV Lines - Rebuild lines between Cliffside 5 and Inman Tie with 1158 ACSS/TW | 3.88 | 2028-11-06
| W230456 | Lawsons Fork Tie Series 100kV BJB | 0.78 | 2030-09-03
| W250223 | Switzer 44 kV Line - Rebuild between structures 48 and 139.5 with 477 ACSS/TW. Includes adding a 100 kV Circuit | 2.31 | 2028-10-23
|  | Total Cost | 76790000