## BranchViol
Case | Monitored Facility | Areas | Rate Cont (MVA) | Contingency Name | Cont Flow (MVA) | Final AC %Loading | Solution
nctpc35w_rob2dn | 304694 KINGS HWY 115 304696 SHAW AFB TAP 115 1 | 340 | 169 | BLCKNICKL-SUMMRTN230_&_SUMT-WATEREE230 | 169 | 99.98 | Existing project to reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F
nctpc35w_rob2dn | 304688 GOLD TAP 115 304694 KINGS HWY 115 1 | 340 | 169 | BLCKNICKL-SUMMRTN230_&_SUMT-WATEREE230 | 167 | 98.82 | Existing project to reconductor the 397.5 ACSR portion (5.82 miles) of Sumter Gold Kist Tap - Sumter Kings Hwy section of Sumter - Eastover 115kV line
nctpc35w_rob2dn | 304694 KINGS HWY 115 304696 SHAW AFB TAP 115 1 | 340 | 169 | SMTCONT-BLCKNICKL_&_SUMT-WATEREE230 | 164.6 | 97.37 | Existing project to reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F
nctpc30w_rob2dn | 304694 KINGS HWY 115 304696 SHAW AFB TAP 115 1 | 340 | 169 | BLCKNICKL-SUMMRTN230_&_SUMT-WATEREE230 | 163.1 | 96.52 | Existing project to reconductor Kings Hwy - Shaw Field - Eastover sections, raise Gold Kist Tap - Str #427 to 212F
nctpc35w_rob2dn | 304688 GOLD TAP 115 304694 KINGS HWY 115 1 | 340 | 169 | SMTCONT-BLCKNICKL_&_SUMT-WATEREE230 | 162.3 | 96.05 | Existing project to reconductor the 397.5 ACSR portion (5.82 miles) of Sumter Gold Kist Tap - Sumter Kings Hwy section of Sumter - Eastover 115kV line
nctpc30w_rob2dn | 304688 GOLD TAP 115 304694 KINGS HWY 115 1 | 340 | 169 | BLCKNICKL-SUMMRTN230_&_SUMT-WATEREE230 | 161.2 | 95.37 | Existing project to reconductor the 397.5 ACSR portion (5.82 miles) of Sumter Gold Kist Tap - Sumter Kings Hwy section of Sumter - Eastover 115kV line
nctpc30w | 304070 PERSON230 TT 230 316281 AC2-100 TAP 230 1 | 340/345 | 824 | WAKE500_CB41 | 784 | 95.14 | Monitor. Only 95.14% loaded
nctpc35w_br2dn | 304662 FLO SUB230TT 230 304659 FLOSUB115WTT 115 1 | 340 | 239 | FLOSUB230TT-FLOSUB115ETT-230-115-#2 | 227.1 | 95.02 | Existing project to upgrade CT ratio and relay settings to get 336 MVA rating for Florence 230/115kV transformer #1

## Projects to Add to Plan
Project | Region | ISD | Estimated Cost
Barnard Creek – Castle Hayne 230kV East line, Upgrade switches 38A-1, 38A-2 to 3000 A and 41B-3 to 2000 A | DEP | 2028-06-01 | 3000000
Method-DPC East Durham 230 kV line upgrade line switches and terminal equipment at both ends to allow full line conductor 2546 A cold winter rating | DEP | 2028-06-01 | 1800000
Wake-Zebulon 230kV line, Upgrade CT ratios and relay settings at Wake, upgrade line switch 42-1, and upgrade CT ratios and relay settings at Zebulon 230, all to 3000 A | DEP | 2028-06-01 | 2600000
Brunswick 1 - Barnard Creek 230kV line, Upgrade OOS relays, CT ratios, line trap, and line switches to allow us of 2806 A line conductor 32F CW rating | DEP | 2028-06-01 | 1800000
Brunswick 2 - Town Creek 230kV line, Upgrade OOS relay to at least 2000 A, preferably 3000 A | DEP | 2029-12-01 | 362000
DEP Total Estimated Cost |  |  | 9562000